

IEEE 80-1996, Draft 7, October, 1996

Guide for Safety in

AC Substation Grounding

Prepared by the Substation Grounding Safety Working Group, D7, of the

Distribution Substation Subcommittee

Copyright ©1996 by The Institute of Electrical and Electronics Engineers, Inc.

345 East 47th Street

New York, NY 10017, USA

All Rights Reserved.

This is an IEEE Standards Project, subject to change.  Permission is hereby granted for IEEE Standards Committee participants to reproduce this document for purposes of IEEE standardization activities, including balloting and coordination.  If this document is to be submitted to ISO or IEC, notification shall be given to the IEEE Copyright Administrator.  Permission is also granted for member bodies and technical committees of ISO and IEC to reproduce this document for purposes of developing a national position.  Other entities seeking permission to reproduce portions of this document for these or other uses must contact the IEEE Standards Department for the appropriate license.  Use of information contained in the unapproved draft is at your own risk.

IEEE Standards Department

Copyright and Permissions

445 Hoes Lane, P.O. Box 1331

Piscataway, NJ 08855-1331, USA

Introduction

(This introduction is not a part of IEEE 80‑199X, Guide for Safety in AC Substation Grounding.)

This fourth edition represents the second major revision of this guide since its first issue in 1961.  Major modifications include the redefinition of simplified equations for calculating touch and step voltages, the introduction of curves to help determine current division,  changes in the criteria for selection of conductors and connections, and additional information on resistivity measurement interpretation and the discussion of multilayer soils.  Other changes and additions were made in the areas of gas‑insulated substations, the derating factor for surface material, equations for calculation of grid resistance and the annexes. The fourth edition thus continues to build upon the foundations laid by three earlier working groups, AIEE Working Group 56.1 and IEEE Working Groups 69.1 and 78.1.

The work of preparing this standard was done by Working Group D7 of the Distribution Substation Subcommittee and was sponsored by the Substation Committee of the IEEE Power Engineering Society.  At the time this guide was completed, the Substation Grounding Safety Working Group, D7, had the following membership:


Richard P. Keil, Chairman 
Jeffrey D. Merryman, Secretary

H. E. Abdallah
L. N. Ferguson
S. G. Patel

K. O. Abledu
J. Fortin
G. J. Paul

B. Y. Afshar
D. L. Garrett
G. Pecora

S. J. Arnot
D. Goetz
A. J. Rodolakis

N. Barbeito
R. Heinrichs
J. Sabath

T. M. Barnes
R. J. Hellweg
M. Scher

C. J. Blattner
D. T. Jones
F. Shainauskas

M. M. Bostic
G. A. Klein
Y. Shertok

A. Byrd
A. E. Kollar
G. Steinman

J. B. Cannon
D. N. Laird
C. Stidham

A. C. Cockerham
M. P. Ly
J. G. Sverak

E. F. Counsel
J. Ma
W. K. Switzer

W. K. Daily
W. M. Malone
B. Thapar

F. Dawalibi
T. S. McLenahan
M. Vainberg

F. A. Denbrock
A. P. Meliopoulos
L. F. Volf, Jr.

W. K. Dick
J. M. Nahman
R. P. Webb

V. L. Dixon
B. P. Ng
R. J. Wehling

S. L. Duong
J. T. Orrell

Contents

CLAUSE
PAGE

1.
Overview
9


1.1
Purpose and scope
9


1.2
Relation and other standards
10

2.
References
11

3.
Definitions
12

4.
Safety in grounding
14


4.1
Basic problem
14


4.2
Conditions of danger
16

5.
Range of tolerable current
18


5.1
Effect of frequency
18


5.2
Effect of magnitude and duration
18


5.3
Importance of high-speed fault clearing
19

6.
Tolerable body current limit
20


6.1
Duration formula
20


6.2
Alternative assumptions
20


6.3
Comparison of Dalziel’s equations and Biegelmeier’s curve
22


6.4
Note of reclosing
23

7.
Accidental ground circuit
24


7.1
Resistance of the human body
24


7.2
Current paths through the body
25


7.3
Accidental circuit equivalents
26


7.4
Effect of a thin surface layer of surface material
28

8.
Criteria of tolerable potential difference
32


8.1
Definitions
32


8.2
Typical shock situations
32


8.3
Step and touch voltage criteria
35


8.4
Typical shock situations for gas-insulated substations
36


8.5
Effect of sustained ground currents
38

9.
Principal design considerations
39


9.1
Definitions
39


9.2
General concept
39


9.3
Primary and auxiliary ground electrodes
40


9.4
Basic aspects of grid design
40


9.5
Design in difficult conditions
41


9.6
Connections to grid
42

10.
Special considerations for gas-insulated substations (GIS)
43


10.1
Definitions
43


10.2
GIS characteristics
43


10.3
Enclosures and circulating currents
43


10.4
Grounding of enclosures
44


10.5
Cooperation between GIS manufacturer and user
44


10.6
Other special aspects of GIS grounding
45


10.7
Notes on grounding of GIS foundations
46


10.8
Touch voltage criteria for GIS
46

11.
Selection of conductors and connections
49


11.1
Basic requirements
49


11.2
Choice of material for conductors and related corrosion problems
49


11.3
Minimum size formula
50


11.4
Selection of connections
58


11.5
Additional conductor sizing factors
59


11.6
Final choice of conductor size
59

12.
Soil characteristics
61


12.1
Soil as a grounding medium
61


12.2
Effect of voltage gradient
61


12.3
Effect of current magnitude
61


12.4
Effect of moisture temperature and chemical content
61


12.5
Use of surface material layer
63

13.
Soil structure and selection of soil model
64


13.1
Investigation of soil structure
64


13.2
Classification of soils and ranges of resistivity
64


13.3
Resistivity measurements
64


13.4
Interpretation of soil resistivity measurements
67


13.5
Uniform soil assumption
68


13.6
Nonuniform soil assumptions
69

14.
Evaluation of ground resistance
73


14.1
Usual requirements
73


14.2
Simplified calculations
73


14.3
Schwarz’s equations
74


14.4
Note on resistance of primary electrodes
76


14.5
Soil treatment to lower resistivity
77


14.6
Concrete - encased electrodes
79

15.
Determination of maximum grid current
83


15.1
Definitions
83


15.2
Procedure

84


15.3
Types of ground faults
84


15.4
Effect of substation ground resistance
89


15.5
Effect of fault resistance
89


15.6
Effect of overhead ground wires and neutral conductors
89


15.7
Effect of direct buried pipes and cables
89


15.8
Worst fault type and locations -- step (a)
90


15.9
Computation of current division -- step (b)
91


15.10
Effect of asymmetry --step (c)
95


15.11
Effect of future changes -- step (d)
98

16.
Design of grounding system
100


16.1
Design criteria
100


16.2
Critical parameters
101


16.3
Index of design parameters
102


16.4
Design procedure
102


16.5
Calculation of maximum step and mesh voltages
103


16.6
Refinement of preliminary design
106


16.7
Application of simplified equation for Em and Es
107


16.8
Use of computer analysis in grid design
107

17.
Investigation of special danger points
111


17.1
Service areas
111


17.2
Switch shaft and operating handle grounding
111


17.3
Grounding of substation fence
113


17.4
Results of voltage profiles for fence grounding
116


17.5
Cable sheath grounding
120


17.6
GIS bus extension
120


17.7
Surge arrester grounding
120


17.8
Note on separate and common grounds
120


17.9
Transferred potentials
120



17.9.1
Communication circuits
121



17.9.2
Rails
121



17.9.3
Low-voltage neutral wires
122



17.9.4
Portable equipment and tools supplied from substation
122



17.9.5
Piping
123



17.9.6
Auxiliary buildings
123



17.9.7
Fences
123

18.
Notes on the construction of a grounding system
125


18.1
Ground-grid construction-trench method
125


18.2
Ground-grid construction-conductor plowing method
125


18.3
Installation of joints, pigtails, and ground rods
126


18.4
Construction sequence consideration for ground-grid installation
126


18.5
Safety considerations during subsequent excavations
126

19.
Field measurements of a constructed grounding system
128


19.1
Measurements of grounding system impedance
128


19.2
Field survey of potential contours and touch and step voltages
130


19.3
Assessment of field measurement for safe design
131


19.4
Periodic checks of installed grounding system
133

20.
Physical scale models
134

Annex A  Bibliography (informative)
134

Annex B  Sample and Calculations (Informative)
1xx


B1.
1xx


B2.
1xx


B3.
1xx


B4..
1xx


B5..
1xx


B6..
1xx

Annex C Graphical and Approximate Analysis of Current Division(Informative)
1xx


C1.
Introduction


C2.


C3.


C4.

Annex D Simplified Equation(Informative)
1xx

Annex E  Equivalent Uniform Soil Model for Non-Uniform Soils (Informative)
1xx

Annex F  Grounding Methods for High Voltage substations with Grounded Neutrals(Informative)
2xx

Index

2xx

FIGURES











PAGE

Figure1

Relationship between actual values of fault current and values of IF, If and Df for 




fault duration tf  .................................................................................................................

Figure2

Typical faulted substation with and without multiple return ground paths............................

Figure3

Equipotential contours of a typical grounding grid with and without ground rods.................

Figure4

Fibrillating current versus body weight for various animals based on a three-second shock..

Figure5

Figure6

Figure7

Figure8

Figure9

Basic shock situations........................................................................................................

Figure10 
Typical situation of external transferred potential................................................................

Figure11
Typical metal-to-metal touch situations in GIS....................................................................

Figure12
Touch voltage limits for metal-to-metal contact and a typical range of enclosure 




voltages to ground..............................................................................................................

Figure13
Typical faults in GIS..........................................................................................................

Figure14

Figure15
Soil Model.........................................................................................................................

Figure16
Effects of moisture, temperature and salt upon soil resistivity..............................................

Figure17

Figure18
Coefficients K1 and K2 of Schwarz’s formula.....................................................................

Figure19
Short-time current loading capability of concrete-encased ground electrodes........................

Figure20
Grid with encased vertical electrodes..................................................................................

Figure21
Fault within local substation; local neutral grounded...........................................................

Figure22
Fault within local substation; neutral grounded at remote location.......................................

Figure23
Fault in substation; system grounded at local substation and also at other points..................

Figure24
Typical current division for a fault on high side of distribution substation............................

Figure25
Example system for computation of current division factor  Sf.............................................

Figure26
Design procedure block diagram.........................................................................................

Figure27
Fall-of-potential method and earth surface potentials for various spacings “X”....................

TABLES

Table 1

Material constants.......................................................................................................

Table 2

Minimum per unit conductor sizes (cmils/A).....................................................................

Table 3

Typical surface material resistivities.................................................................................

Table 4

Range of earth resistivity..................................................................................................

Table 5

Typical grid resistances....................................................................................................

Table 6

Typical Values of Df .......................................................................................................

Table 7

Typical ratio of corner-to-corner mesh voltage..................................................................

Table 8

Index of design parameters...............................................................................................

ANNEX FIGURES









PAGES

Figure A1

ANNEX TABLES

Table A1

Guide for Safety in

AC Substation Grounding

1.  Overview
1.1  Scope

This guide is primarily concerned with outdoor ac substations, either conventional or gas-insulated.  These include distribution, transmission, and generating plant substations.  With proper caution, the methods described herein are also applicable to indoor portions of such substations, or to substations that are wholly indoors.

No attempt is made to cover the grounding problems peculiar to dc substations.  A quantitative analysis of the effects of lightning surges is also beyond the scope of this guide.
1.2  Purpose

The intent of this guide is to provide guidance and information pertinent to safe grounding practices in ac substation design.

The specific purposes of this guide are:

a) To establish, as a basis for design, the safe limits of potential differences that can exist in a substation under fault conditions between points that can be contacted by the human body

b) To review substation grounding practices with special reference to safety, and develop criteria for a safe design

c) To provide a procedure for the design of practical grounding systems, based on these criteria

d) To develop analytical methods as an aid in the understanding and solution of typical gradient problems

The concept and use of safety criteria are described in clauses 1‑8, practical aspects of designing a grounding system are covered in clauses 9-13, and procedures and evaluation techniques for the grounding system assessment (in terms of safety criteria) are described in clauses 14-20.  Supporting material is organized in annexes A-F.

This guide is primarily concerned with safe grounding practices for power frequencies in the range of 50-60 Hz.  The problems peculiar to dc substations and the effects of lightning surges are beyond the scope of this guide.  A grounding system  designed as recommended herein will, nonetheless, provide some degree of protection against steep wave front surges entering the substation and passing to earth through its ground electrodes.
   Other references should be consulted for more information about these subjects.

1.3  Relation to other standards

This guide only briefly discusses the field tests required to evaluate soil resistivity.  The procedures for measuring the earth resistivity, the resistance of the installed grounding system, the surface gradients, and the continuity of the grid conductors are described in more detail in IEEE Std 81‑1983 and IEEE Std 81.2-1991.

IEEE Std 142‑1991 generally takes its recommended grounding prac​tices from this guide.  Also known as "The IEEE Green Book," it covers some of the practical aspects of grounding in more detail, such as equipment grounding, cable routing to avoid induced ground currents, cable sheath grounding, static and lightning protection, indoor installations, etc.

IEEE Std 367‑1987 provides a detailed explanation of the asymmetrical current phenomenon and of the fault current division, which to a large degree parallels that given herein.  Of course, the reader should be aware that the ground potential rise calculated for the purpose of telecommunication protection and relaying applications is based on a somewhat different set of assumptions con​cerning the maximum grid current, in comparison with those used for the pur​poses of this guide.

IEEE Std 665-1995 provides a detailed explanation of generating station grounding practices.

IEEE Std 837-1989 (Reaff. 1995) provides tests and criteria to select connections to be used in the grounding system that will meet the concerns described in clause 11.

2.  References

This guide should be used in conjunction with the following publications.  When the following standards are superseded by an approved revision, the revision shall apply.

C2‑1997, National Electrical Safety Code (note particularly Rule 93C) (ANSI).

IEEE Std 81‑1983, IEEE Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Surface Potentials of a Ground System ‑ Part I: Normal Measurements (ANSI) 
.

IEEE Std 81.2‑1991, IEEE Guide for Measurement of Impedance and Safety Characteristics of Large, Extended or Interconnected Grounding Systems(ANSI).

IEEE Std 100‑1992, IEEE Standard Dictionary of Electrical and Electronics Terms (ANSI).

IEEE Std 142‑1991, IEEE Recommended Practice for Grounding of Industrial and Commercial Power Systems (ANSI).

IEEE Std 367‑1987, IEEE Guide for the Maximum Electric Power  Substation Ground Potential Rise and Induced Voltage from a Power Fault. 

IEEE Std 525-1992, IEEE Guide for the Design and Installation of Cable Systems in Substations.

IEEE Std 665-1995, IEEE Guide for Generating Station Grounding.

IEEE Std 837‑1989 (Reaff. 1995), IEEE Standard for Qualifying Permanent Connections Used in Substation Grounding (ANSI).

3.  Definitions

Most of the definitions given herein pertain solely to the application of this guide.  No further references will be made to any of the definitions stated below, unless necessary for clarity.  All other definitions are placed within the text of individual clauses.  For additional definitions refer to IEEE Std 100-1992.

3.1  auxiliary ground electrode:  A ground electrode with certain design or operating constraints.  Its primary function may be other than conducting the ground fault current into the earth.

3.2  continuous enclosure:  A bus enclosure in which the consecutive sections of the housing along the same phase conductor are bonded together to provide an electrically continuous current path throughout the entire enclosure length.  Cross-bondings, connecting the other phase enclosures, are made only at the extremities of the installation and at a few selected intermediate points.

3.3  dc offset: Difference between the symmetrical current wave and the actual current wave during a power system transient condition.  Mathematically, the actual fault current can be broken into two parts, a symmetrical alternating component and a unidirectional (dc) component, either or both with decreasing magnitudes (usually both).  The unidirectional component can be of either polarity, but will not change polarity, and will decrease at some predetermined rate.

3.4  dc offset factor:  Ratio of the peak fault current to the peak symmetrical value.

3.5  decrement factor:  An adjustment factor used in conjunction with the symmetrical ground fault current parameter in safety‑oriented grounding calculations.  It determines an rms equivalent of the asymmetrical current wave for a given fault duration, tf, for tf given in s, accounting for the effect of initial dc offset and its attenuation during the fault.

3.6  effective asymmetrical fault current:  The rms value of asymmetrical current wave, integrated over the interval of fault duration.       (See figure 3-1.)

NOTE: In terms of this guide, it can be expressed as





(1)
where

IF
is the effective asymmetrical fault current in A

If  
is the rms symmetrical ground fault current in A

Df
is the decrement factor

 FIGURE 3-1 {old Fig 1}
Figure3-1
Relationship between actual values of fault current and 

values of IF, if, and Df for fault duration tf
3.7  enclosure currents:  Currents that result from the voltages induced in the metallic enclosure by the current(s) flowing in the enclosed conductor(s).

3.8  fault current division factor:  A factor representing the inverse of a ratio of the symmetrical fault current to that portion of this current that flows between the grounding grid and surrounding earth.

NOTE:  For the purposes of calculating the design value of maximum grid current and symmetrical grid current per definitions of symmetrical grid current and maximum grid current, it may be assumed that the ratio is constant during the entire duration of a given fault.  Consequently, this factor may be expressed as





(2)

where

Ig
is the rms symmetrical grid current

I0
is the zero‑sequence fault current

3.9  gas-insulated substation:  A compact, multicomponent assembly, enclosed in a grounded metallic housing in which the primary insulating medium is a com​pressed gas, and that normally consists of buses, switchgear, and associated equipment (subassemblies).

3.10  ground:  A conducting connection, whether intentional or accidental, by which an electric circuit or equipment is connected to the earth or to some conducting body of relatively large extent that serves in place of the earth.

3.11  grounded:  A system, circuit, or apparatus provided with a ground(s) for the purposes of establishing a ground return circuit and for maintaining its potential at approximately the potential of earth.

3.12  ground current:  A current flowing into or out of the earth or its equivalent serving as a ground.

3.13  ground electrode:  A conductor imbedded in the earth and used for collecting ground current from or dissipating ground current into the earth.

3.14  ground mat:  A solid metallic plate or a system of closely spaced bare conductors that are connected to and often placed in shallow depths above a ground grid or elsewhere at the earth surface, in order to obtain an extra protective measure minimizing the danger of the exposure to high step or touch voltages in a critical operating area or places that are frequently used by people.  Grounded metal gratings, placed on or above the soil surface, or wire mesh placed directly under the surface material, are common forms of a ground mat.

3.15  ground potential rise (GPR):  The maximum electrical potential that a substation grounding grid may attain relative to a distant grounding point assumed to be at the potential of remote earth.

NOTE:  Under normal conditions, the grounded electrical equipment operates at near zero ground potential.  That is, the potential of a grounded neutral conductor is nearly identical to the potential of remote earth.  During a ground fault the portion of fault current that is conducted by a substation grounding grid into the earth causes the rise of the grid potential with respect to remote earth.  This voltage, the GPR, is proportional to the magnitude of the grid current, and to the grid resistance. 

3.16  ground return circuit:  A circuit in which the earth or an equivalent conducting body is utilized to complete the circuit and allow current circulation from or to its current source.

3.17  grounding grid:  A system of horizontal ground electrodes that consists of a number of interconnected, bare conductors buried in the earth, providing a com​mon ground for electrical devices or metallic structures, usually in one specific location.

NOTE:  Grids buried horizontally near the earth's surface are also effective in controlling the surface from potential gradients.  A typical grid usually is supplemented by a number of ground rods and may be further connected to auxiliary ground electrodes to lower its resistance with respect to remote earth.

3.18  grounding system:  Comprises all interconnected grounding facilities in a specific area.

3.19  symmetrical ground fault current:  The maximum rms value of symmetrical fault current after the instant of a ground fault initiation.  As such, it represents the rms value of the symmetrical component in the first half‑cycle of a current wave that develops after the instant of fault at time zero.  For phase-to-ground faults,






 INCRUSTAR Equation.2  

(3)

where




is the initial rms symmetrical ground fault current




is the rms value of zero‑sequence symmetrical current that develops immediately after the instant of fault initiation, reflecting the subtransient reactances of rotating machines contributing to the fault

This rms symmetrical fault current is shown in an abbreviated nota​tion, as If, or is referred to only as 3I0.  The underlying reason for the latter notation is that, for purposes of this guide, the initial symmetrical fault current is assumed to remain constant for the entire duration of the fault.

3.20  main ground bus:  A conductor or system of conductors provided for connecting all designated metallic components of the GIS to a substation grounding system.

3.21  maximum grid current:  A design value of the maximum grid current,  defined as follows:





(4)

where

IG
is the maximum grid current in A

Df
is the decrement factor for the entire duration of fault tf, given in s

Ig
is the rms symmetrical grid current in A

3.22  mesh voltage: The maximum touch voltage within a mesh of a ground grid.

3.23  metal-to-metal touch voltage:  The voltage between metallic objects or structures within the substation site that may be bridged by direct hand-to-hand or hand-to-feet contact.

NOTE:  The metal-to-metal touch voltage between metallic objects or structures bonded to the ground grid is assumed to be negligible in conventional substations.  However, the metal-to-metal touch voltage between metallic objects or structures bonded to the ground grid and metallic objects internal to the substation site, such as an isolated fence, but not bonded to the ground grid may be substantial.  In the case of gas-insulated substations, the metal-to-metal touch voltage between metallic objects or structures bonded to the ground grid may be substantial because of internal faults or induced currents in the enclosures.

In a conventional substation, the worst touch voltage is usually found to be the potential difference between a hand and the feet at a point of maximum reach distance.  However, in the case of a metal-to-metal contact from hand-to-hand or from  hand-to-feet, both situations should be investigated for the possible worst reach conditions.  Figures 8-1 and 8-2 illustrate these situations for air-insulated substations, and figure 8-3 illustrates these situations in GIS.

3.24  noncontinuous enclosure:  A bus enclosure with the consecutive sections of the housing of the same phase conductor electrically isolated (or insulated from each other), so that no current can flow beyond each enclosure section.

3.25  primary ground electrode:  A ground electrode specifically designed or adapted for discharging the ground fault current into the ground, often in a specific dis​charge pattern, as required (or implicitly called for) by the grounding system design.

3.26  step voltage:  The difference in surface potential experienced by a person bridging a distance of 1m with the feet without contacting any grounded object.

3.27  subtransient reactance:  Reactance of a generator at the initiation of a fault.  This reactance is used in calculations of the initial symmetrical fault current.  The current continuously decreases, but it is assumed to be steady at this value as a first step, lasting approximately 0.05 s after an applied fault.

3.28  surface material:  A material installed over the soil consisting of, but not limited to, rock or crushed stone, asphalt, or man-made materials.  The surfacing material, depending on the resistivity of the material, may significantly impact the body current for touch and step voltages involving the person’s feet.

3.29  symmetrical grid current:  That portion of the symmetrical ground  fault current that flows between the grounding grid and surrounding earth.  It may be expressed as:





(5)

where

Ig
is the symmetrical grid current in A

If
is the rms symmetrical ground fault current in A

Sf
is the current division factor relating the magnitude of fault current to that portion of this current flowing between the grounding grid and surrounding earth

3.30  touch voltage:  The potential difference between the ground potential rise (GPR) and the surface potential at the point where a person is standing while at the same time having a hand in contact with a grounded structure.

3.31  transferred voltage:  A special case of the touch voltage where a voltage is transferred into or out of the substation from or to a remote point external to the substation site.

3.32  transient  enclosure voltage (TEV):  Very fast transient phenomena, which are found on the grounded enclosure of GIS systems.  Typically, ground leads are too long (inductive) at the frequencies of interest to effectively prevent the occurrence of TEV.  The phenomenon is also known as transient ground rise (TGR) or transient ground potential rise (TGPR). [B1???], [B2???] from Peter Dick

3.33  very fast transient (VFT):  A class of transients generated internally within GIS characterized by short duration and very high frequency nature [1].  VFT is generated by the rapid collapse of voltage during breakdown of the SF6 insulating gas, either across the contacts of a switching device or line-to-ground during a fault.  These transients can have rise times in the order of nanoseconds implying a frequency content extending to about 100 MHz.  However, dominant oscillation frequencies, which are related to physical lengths of GIS bus are usually in the 20-40 Mhz range. 

3.34  very fast transients overvoltage (VFTO):  System overvoltages which result from generation of VFT.  While VFT are one of the main constituents of VFTO, some lower frequency (( 1 MHz) component may be present as a result of the discharge of lumped capacitance (PTs, CVTs, etc.).  Typically, VFTO will not exceed 2.0 per unit although higher magnitudes are possible in specific instances. [B1??? from Peter Dick]

3.35  X/R ratio:  Ratio of the system reactance to resistance.  It is indicative of the rate of decay of any dc offset.  A large X/R ratio corresponds to a large time constant and a slow rate of decay.

4.  Safety in grounding

4.1  Basic problem

In principle, a safe grounding design has two objectives:

- To provide means to carry electric currents into the earth under normal and fault conditions without exceeding any operating and equipment limits or adversely affecting continuity of service

- To assure that a person in the vicinity of grounded facilities is not exposed to the danger of critical electric shock

A practical approach to safe grounding thus concerns and strives for control​ling the interaction of two grounding systems:

- The intentional ground, consisting of ground electrodes buried at some depth below the earth surface

- The accidental ground, temporarily established by a person exposed to a potential gradient in the vicinity of a grounded facility

People often assume that any grounded object can be safely touched.  A low substation ground resistance is not, in itself, a guarantee of safety.  There is no simple relation between the resistance of the ground system as a whole and the maximum shock current to which a person might be exposed.  Therefore, a substation of relatively low ground resistance may be dangerous, while another substation with very high resistance may be safe or can be made safe by careful design.  For instance, if a substation is supplied from an overhead line with no shield or neutral wire, a low grid resistance is important.  Most or all of the total ground fault current enters the earth causing an often steep rise of the local ground potential; figure 4-1(a).  If a shield wire, neutral wire, gas‑insulated bus, or underground cable feeder, etc., is used, a part of the fault current returns through this metallic path directly to the source. Since this metallic link provides a low impedance parallel path to the return cir​cuit, the rise of local ground potential is ultimately of lesser magnitude; figure 4-1(b).  In either case, the effect of that portion of fault current that enters the earth within the substation area should be further analyzed.  If the geometry, location of ground electrodes, local soil characteristics, and other factors contribute to an excessive potential gradient at the earth surface, the grounding system may be inadequate despite its capacity to carry the fault current in magnitudes and durations permitted by protective relays.

The following clauses 5 through 8 cover in detail those principal assumptions and criteria that enable the evaluation of all necessary factors in protecting the most precious element of the accidental circuit, human life.

FIGURE 4-1 [old Fig 2}

                         (a)                                                                                                             (b)
Figure 4-1

Typical faulted substation with and without multiple ground return paths
4.2  Conditions of danger

During typical ground fault conditions, the flow of current to earth will produce potential gradients within and around a substation. Figure 4-2 shows this effect for a substation with a simple rectangular grounding grid in homogeneous soil.

FIGURE 4-2 [old Fig 3}
Figure 4-2
Equipotential contours of a typical grounding grid
with and without ground rods

Unless proper precautions are taken in design, the maximum potential gradients along the earth surface may be of sufficient magnitude during ground fault conditions to endanger a person in the area.  Moreover, dangerous voltages may develop between grounded structures or equipment frames and the nearby earth.

The circumstances that make electric shock accidents possible are:

a) Relatively high fault current to ground in relation to the area of ground system and its resistance to remote earth

b) Soil resistivity and distribution of ground currents such that high potential gradients may occur at points at the earth surface

c) Presence of an individual at such a point, time, and position that the body is bridging two points of high potential difference

d) Absence of sufficient contact resistance or other series resistance to limit current through the body to a safe value under the above circumstances

e) Duration of the fault and body contact, and hence, of the flow of current through a human body for a sufficient time to cause harm at the given current intensity

The relative infrequency of accidents is due largely to the low probability of coincidence of all the unfavorable conditions mentioned above.

5.  Range of tolerable current

Effects of an electric current passing through the vital parts of a human body depend on the duration, magnitude, and frequency of this current.  The most dangerous consequence of such an exposure is a heart condition known as ven​tricular fibrillation, resulting in immediate arrest of blood circulation.

5.1  Effect of frequency

Humans are very vulnerable to the effects of electric current at frequencies of 50 or 60 Hz.  Currents of approximately 0.1 A can be lethal. Authorities generally agree that the human body can tolerate a slightly higher 25 Hz current and approximately five times higher direct current.  At frequencies of 3000‑10000 Hz, even higher currents can be tolerated. [B35], [B37]
  In some cases the human body is able to tolerate very high currents due to lightning surges.  The IEC provides curves for the tolerable body current as a function of frequency and for capacitive discharge currents. [B?? (IEC 479-2)]  Other studies of the effects of both direct and oscillatory impulse currents are reported in the literature. [B26], [B28]

Information regarding special problems of dc grounding is contained in the 1958 Report of the Conversion Substation Committee. [B23]  The hazards of an electric shock produced by the electrostatic effects of overhead transmission lines are reviewed in Part 1 of the 1971 Report of the General Substations Subcommittee. [B76]  Additional information on the electrostatic effects of overhead trans​mission lines can be found in Chapter 8 of. [B58]

5.2  Effect of magnitude and duration

The most common physiological effects of electric current on the body, stated in order of increasing current magnitude, are perception, muscular contraction, unconsciousness, fibrillation of the heart, respiratory nerve blockage, and burning. [B70], [B?? (IEC 479-1)]

Current of 1mA is generally recognized as the threshold of perception, that is, the current magnitude at which a person is just able to detect a slight tingling sensation in his hands or fingertips caused by the passing current. [B28]

Currents of 1‑6 mA, often termed let‑go currents, though unpleasant to sustain, generally do not impair the ability of a person holding an energized object to control his muscles and release it.  Dalziel's classic experiment with 28 women and 134 men provides data indicating an average let‑go current of 10.5 mA for women and 16 mA for men, and 6 mA and 9 mA as the respective threshold values. [B36]  

In a 9‑25 mA range, currents may be painful and can make it difficult or impossi​ble to release energized objects grasped by the hand.  For still higher currents muscular contractions could make breathing difficult.  Unlike the cases of respira​tory inhibition from the much greater current mentioned next, these effects are not permanent and disappear when the current is interrupted, unless the con​traction is very severe and breathing is stopped, not for seconds, but for minutes.  Yet even such cases often respond to resuscitation. [B32]

It is not until current magnitudes in the range of 60‑100 mA are reached that ventricular fibrillation, stoppage of the heart, or inhibition of respiration might occur and cause injury or death.  A person trained in cardiopulmonary resuscitation should administer CPR until the victim can be treated at a medical facility. [B34]

Hence, this guide emphasizes the importance of the fibrillation threshold.  If shock currents can be kept below this value by a carefully designed grounding system, injury or death may be avoided.

As shown by Dalziel and others [B33], [B36], the nonfibrilating current of magnitude IB at durations ranging from 0.03‑3.0 s is related to the energy absorbed by the body as described by the following equation:





(6)
where

IB
is the rms magnitude of the current through the body in A

ts
is the duration of the current exposure in s
SB
is the empirical constant related to the electric shock energy tolerated by a cer​tain percent of a given population

A more detailed discussion of this equation is provided in clause 6.

5.3  Importance of high‑speed fault clearing

Considering the significance of fault duration both in terms of equation (6) and implicitly as an accident‑ exposure factor, high‑speed clearing of ground faults is advantageous for two reasons:

a) The probability of electric shock is greatly reduced by fast fault clearing time, in contrast to situations in which fault currents could persist for several minutes or possibly hours.

b) Both tests and experience show that the chance of severe injury or death is greatly reduced if the duration of a current flow through the body is very brief.  The allowed current value may therefore be based on the clearing time of primary protective devices, or that of the back‑up protection.

A good case could be made for using the primary clearing time because of the low combined proba​bility that relay malfunctions will coincide with all other adverse factors necessary for an accident, as has already been described in clause 4.

If the probabilistic aspects are neglected, it is more conservative to choose the backup relay clearing times in equation (6), because it assures greater safety margin.

An additional incentive to use switching times less than 0.5 s results from the research done by Biegelmeier and Lee [B11].  Their research provides evidence that a human heart becomes increasingly susceptible to ventricular fibrillation when the time of exposure to current is approaching the heartbeat period,  but that the danger is much smaller if the time of exposure to current is in the region of 0.06‑0.3 s.

In reality, high ground gradients from faults are usually infrequent, and shocks from this cause still more so.  Furthermore, both events are often of very short duration. Thus, it would not be practical to design against shocks that are merely painful and cause no serious injury, that is, for currents below the  fibrillation threshold.

6.  Tolerable body current limit

The magnitude and duration of the current conducted through a human body at 50 or 60 Hz should be less than the value that can cause ventricular fibrillation of the heart.

6.1  Duration formula

The duration for which a 50 or 60 Hz current can be tolerated by most people is related to its magnitude in accordance with equation (6). Based on the results of Dalziel's studies [B27], [B31], it is assumed that 99.5% of all persons can safely withstand, without ventricular fibrillation, the passage of a current with magnitude and duration determined by the following formula:





(7)

where, in addition to the terms previously defined, for equation (6), 





Dalziel found that the shock energy that can be survived by 99.5% of persons weighing approximately 50 kg (110 lbs) results in a value of SB of 0.0135. Thus, k50 = 0.116 and the formula for the allowable body current becomes





for 50 kg body weight
(8)

Note that the above equation results in values of 116 mA for ts = 1 s and 367 mA for ts = 0.1 s.

Because equation (7) is based on tests limited to a range of between 0.03‑3.0 s, it obviously is not valid for very short or long durations.

Over the years, other researchers have suggested other values for IB.  In 1936 Ferris et al. [B65] suggested 100 mA as the fibrillation threshold. The value of 100 mA was derived from extensive experiments at Columbia University on animals having body and heart weights comparable to a human, for a maximum shock duration of 3 s. Some of the more recent experiments suggest the existence of two distinct thresholds: one where the shock duration is shorter than one heartbeat period and another one for the current duration longer than one heartbeat.  For a 50 kg (110 lbs) adult, Biegelmeier proposed the threshold values at 500 mA and 50 mA, respectively. [B9], [B10]  Other studies on this subject were carried out by Lee and Kouwenhoven. [B34], [B84], [B89]  The equation for tolerable body current developed by Dalziel is the basis for the derivation of tolerable voltages used in this guide.

6.2  Alternative assumptions

Fibrillation current is assumed to be a function of individual body weight, as illustrated in figure 6-1. This shows the relationship between the critical current and body weight for several species of animals (calves, dogs, sheep, pigs), and a 0.5% common threshold region for mammals.

In the 1961 edition of this guide, constants SB and k in equations (6) and (7), were given as 0.0272 and 0.165, respectively, and had been assumed valid for 99.5% of all people weigh​ing approximately 70 kg (155 lbs).  Further studies by Dalziel [B29] [B31], on which equation (7) is based, lead to the alternate value of k = 0.157 and SB = 0.0246 as being applicable to persons weighing 70 kg (155 lbs).  Thus,





for 70kg body weight
(9)

Users of this guide may select k = 0.157 provided that the average population weight can be expected to be at least 70 kg.

Equation (7) indicates that much higher body currents can be allowed where fast operating protective devices can be relied upon to limit the fault duration.  A judgment decision is needed as to whether to use the clearing time of primary high-speed relays, or that of the back‑up protection, as the basis for calculation.

FIGURE 6-1 {old fig 4}
Figure 6-1
Fibrillating current versus body weight for various animals
based on a three-second duration of the electrical shock

6.3  Comparison of Dalziel’s equations and Biegelmeier’s curve

The comparison of equations (8), (9) and the Z-shaped curve of body current versus time developed by Biegelmeier that was published by G. Biegelmeier and W. R. Lee [B11] is shown below in figure 6-2.  The Z curve has a 500 mA limit for short times up to 0.2 s, then decreasing to 50 mA at 2.0 s and beyond.

Using equation (8), the tolerable body current will be less than Biegelmeier’s Z curve for times from 0.06 s to 0.7 s.

FIGURE 6-2 {new fig from Don Laird}
Figure 6-2
Body current versus time

6.4  Note on reclosing

Reclosure after a ground fault is common in modern operating practice.  In such circumstances, a person might be subjected to the first shock without permanent injury.  Next, a single instantaneous automatic reclosure could result in a second shock, initiated within less than 0.33 s from the start of the first.  It is this second shock, occurring after a relatively short interval of time before the person has recovered, that might cause a serious accident.  With manual reclosure, the possi​bility of exposure to a second shock is reduced because the reclosing time interval may be substantially greater.

The cumulative effect of two or more closely spaced shocks has not been thoroughly evaluated, but a reasonable allowance can be made by using the sum of individual shock durations as the time of a single exposure.

7.  Accidental ground circuit

7.1  Resistance of the human body

For dc and 50 Hz or 60 Hz ac currents, the human body can be approximated by a resistance.  The current path typically considered is between one hand to both feet, or from one foot to the other one.  The internal resistance of the body is approximately 300 , as suggested in the literature. [B27], [B70], [B71], [B83], [B110]  The human body resistance is decreased by damage or puncture of the skin at the point of contact.
, whereas values of body resistance including skin range from 500 to 3000 
As mentioned in 5.2, Dalziel conducted extensive tests to determine safe let-go currents, with hands and feet wet, in salt water.  Values obtained using 60 Hz for men were as follows: the current was 9.0 mA; corresponding voltages were, hand-to-hand, 21.0 V, and, hand-to-feet, 10.2 V. Hence, the ac resistance for a hand-to-hand contact is equal to 21.0/0.009 or 2330 , based on this experiment. [B36]
 and the hand-to-feet resistance equals 10.2/0.009 or 1130 
Thus, for the purposes of this guide, the following resistances, in series with the body resistance, are assumed as follows:

a) Hand and foot contact resistances are equal to zero.

b) Glove and shoe resistances are equal to zero.

A value of 1000  is selected for the calculations that follow as representing the resistance of a human body from hand-to-both-feet and also from hand-to-hand, or from one foot to the other foot:


RB = 1000 
(10)

7.2  Current paths through the body

It should be remembered that the choice of a 1000  resistance value relates to paths such as those between the hand and one or both feet, where a major part of the current passes through parts of the body containing vital organs, including the heart.  It is generally agreed that current flowing from one foot to the other is far less dangerous.  Referring to tests done in Germany, Loucks mentioned that much higher foot-to-foot than hand-to-foot currents had to be used to produce the same current in the heart region, stating that the ratio is as high as 25:1 [B90].

Based on these conclusions, resistance values greater than 1000  could  possibly be allowed, where a path from one foot to the other foot is concerned.  However, the following factors should be considered:

a) A voltage between the two feet, painful but not fatal, might result in a fall that could cause a larger current flow through the chest area.  The degree of this hazard would further depend on the fault duration and the possibility of another, successive shock, perhaps on reclosure.

b) A person might be working or resting in a prone position when a fault, occurs.

It is apparent that the dangers from foot‑to‑foot contact are far less than from the other type.  However, since deaths have occurred from case (a), above, it is a danger that should not be ignored [B17], [B85].

7.3  Accidental circuit equivalents

Using the value of tolerable body current established by equation (8) or (9) and the appropriate circuit constants, it is possible to determine the tolerable voltage between any two points of contact.

The following notations are used for the accidental circuit equivalent which is shown in figure 7-1:

Ib 
is the body current (body is part of the accidental circuit)

RA
is the total effective resistance of the accidental circuit

VA 
is the total effective voltage of the accidental circuit (touch or step voltage)

The tolerable body current, IB , defined by equation (8) or (9), is used to define the tolerable total effective voltage of the accidental circuit (touch or step voltage):  the tolerable total effective voltage of the accidental circuit is that voltage which will cause the flow of a body current, Ib, equal to the tolerable body current, IB.

Figure 7-1 shows the fault current If being discharged to the ground by the grounding system of the substation and a person touching a grounded metallic structure at H.  Various impedances in the circuit are shown in figure 7-2.  Terminal H is a point in the system at the same potential as the grid into which the fault current flows and  terminal F is the small area on the surface of the earth which is in contact with the person's two feet.  The current, Ib, flows from H through the body of the person to the ground at F.  The Thevenin theorem allows us to represent this two terminal (H, F) network of figure 7-2 by the circuit shown in figure -3.  [B45], [B46] 

The Thevenin voltage VTh is the voltage between terminal H and F when the person is not present.  The Thevenin impedance ZTh is the impedance of the system as seen from points H and F with voltage sources of the system short circuited.  The current Ib through the body of a person coming in contact with H and F is given by:





(11)

where


RB
is the resistance of the human body.

The Thevenin equivalent resistance,  is computable with a number of methods. [B45], [B46], [B61], [B141], [B88]  In this guide, the following conservative formulas for the Thevenin equivalent resistance are used:

for touch voltage accidental circuit




(12)

and for the step voltage accidental circuit





(13)

where

Rf 
is the ground resistance of one foot (with presence of the substation grounding system ignored)

For the purpose of circuit analysis, the human foot is usually represented as a conducting metallic disc and the contact resistance of shoes, socks etc is neglected.  The ground resistance in ohms of a metallic disc of radius b (m) on the surface of a homogeneous earth of resistivity -m) is given by  [B88]:
 (




(14)

Traditionally the metallic disc representing the foot is taken as a circular plate of radius 0.08 m.  With only slight approximation, equations for ZTh can be obtained in numerical form and expressed in terms of  as shown below

for touch voltage accidental circuit




(15)

and for step voltage accidental circuit




(16)
Based on investigations reported in [x,x,x], the above equations are conservative in the sense that they underestimate the Thevenin equivalent impedance and, therefore, will result in higher body currents.
The permissible total equivalent voltage (i.e. tolerable touch and step voltage), using the above expressions are:





(17)

and





(18)

7.4  Effect of a thin layer of surface material

Equation (14) is based on the assumption of uniform soil resistivity.  However, a 0.08-0.15 m (3-6 in) layer of high resistivity material, such as gravel, is often spread on the earth's surface above the ground grid to increase the contact resistance between the soil and the feet of people in the substation.  The relatively shallow depth of the surface material as compared to the equivalent radius of the foot precludes the assumption of uniform resistivity in the vertical direction when computing the ground resistance of the feet.  However, for a person in the substation area, the surface material can be assumed to be of infinite extent in the lateral direction.

If the underlying soil has a lower resistivity than the surface material, only some grid current will go upward into the thin layer of the surface material, and the surface voltage will be very nearly the same as that without the  surface material.  The current through the body will be lowered considerably with the addition of the surface material because of the greater contact resistance between the earth and the feet.  However, this resistance may be considerably less than that of a surface layer thick enough to assume uniform resistivity in all directions.  The reduction depends on the relative values of the soil and the surface material resistivities and on the thickness of the surface material.

An analytical expression for the ground resistance of the foot on a thin layer of surface material can be obtained with the use of the method of images.
 [B129], [B140], [B141]

The following equations give the ground resistance of the foot on the surface material. [B141]





(21)




 
(22)





(23)

where

s
is the surface material resistivity, (-m


is the resistivity of the first few meters of earth beneath the surface material, (-m

h
is the thickness of the surface material, m

b
is the radius of the circular metallic disc representing the foot, m

Rm(2nh)
is the mutual ground resistance between the two similar, parallel, coaxial plates, separated by a distance (2nh), in an infinite medium of resistivity s
Determination of Rm(2nh):  Consider a thin circular plate, D1, in the x-y plane with the z axis passing through its center.  The radius of the plate is b and it discharges a current I in an infinite uniform medium of resistivity s.  Using cylindrical coordinates, the potential at any point (r,z) is given by the following equations. [B78]





(24)





(25)

Consider another similar plate, D2, placed parallel and coaxial to the circular plate D1 and at a distance (2nh) from it.  The potential produced on D2 can be determined by evaluating the average potential over the surface of the plate.  It is given by:





(26)

where r is given by equation (24) and z=2nh. Vr,z is given by equation (25).

The mutual ground resistance, Rm(2nh), between the two plates is given by:





(27)

Comparing equations (14) and  (21), Cs can be considered as a corrective factor to compute the effective foot resistance in the presence of a finite thickness of surface material.  Because the quantity Cs  is rather tedious to evaluate without the use of a computer, these values have been precalculated for b=0.08 m and are given in the form of graphs in figure 7-6.

Computer models have also been used to determine the value of Cs.. [B46], [B94]  There is a close match in the values obtained from these computer models with the values given in figure 7-6. 

The following empirical equation gives the value of Cs .  The values of Cs  obtained using equation (28) are very close to the values obtained with the analytical method. [B141]





(28)

Where h and b are both in meters, and the tan-1 is in radians.  This equation is applicable for h varying from 0 to 0.3 m and K varying from 0 to -0.98.  The error in the empirical equation as compared with the analytical method is less than 5%.[B141]

Example.  Let a layer of surface material be 0.1 m (4 in) thick and have the wet resistivity of 2000 -m; b = 0.08 m.  From this data it follows that 
-m; the underlying soil resistivity is 222 
K = -0.8

Cs = 0.725
(From the empirical equation (28).  Figure 7-6 also gives the same value).

R2fp = 1.5 Cs .
s = 2175
R2fs = 6.0 Cs .
s = 8700
Figure 7-6
New curves from 7/18/94 draft

similiar to old fig 8

Figure 7-6

Cs versus h
8.  Criteria of tolerable voltage
8.1  Definitions

8.1.1  ground potential rise (GPR):  The maximum voltage that a substation grounding grid may attain relative to a distant grounding point assumed to be at the potential of remote earth.

NOTE:  Under normal conditions, the grounded electrical equipment operates at near zero ground potential, that is, the potential of a grounded neutral conductor is nearly identical to the potential of remote earth.  During a ground fault the portion of fault current that is conducted by a substation grounding grid into the earth causes the rise of the grid potential with respect to remote earth.  This voltage rise, GPR, is proportional to the magnitude of the grid current, and to the grid resistance. 

8.1.2  step voltage:  The difference in surface potential experienced by a person bridging a distance of 1 m with his feet without contacting any other grounded object.

8.1.3  touch voltage:  The potential difference between the ground potential rise (GPR) and the surface potential at the point where a person is standing while at the same time having his hand in contact with a grounded structure.

8.1.4  metal-to-metal touch voltage:  The difference in potential between metallic objects or structures within the substation site that may be bridged by direct hand-to-hand or hand-to-feet contact.

NOTE:  The metal-to-metal touch voltage between metallic objects or structures bonded to the ground grid is assumed to be negligible in conventional substations.  However, the metal-to-metal touch voltage between metallic objects or structures bonded to the ground grid and metallic objects internal to the substation site, such as an isolated fence, but not bonded to the ground grid may be substantial.  In the case of gas-insulated substations, the metal-to-metal touch voltage between metallic objects or structures bonded to the ground grid may be substantial because of internal faults or induced currents in the enclosures.

In a conventional substation, the worst touch voltage is usually found to be the potential difference between a hand and the feet at a point of maximum reach distance.  However, in the case of a metal-to-metal contact from hand-to-hand or from  hand-to-feet, both situations should be investigated for the possible worst reach conditions. Figures 8-1 and 8-2 illustrate these situations for air-insulated substations, and figure 8-3 illustrates these situations in GIS.

8.1.5  mesh voltage:  The maximum touch voltage within a mesh of a ground grid.

8.1.6  transferred voltage:  A special case of the touch voltage where a voltage is transferred into or out of the substation from or to a remote point external to the substation site.

8.2  Typical shock situations

Figures 8-1 and 8-2 show five basic situations involving a person and grounded facilities during a fault.  For a foot-to-foot contact, the accidental circuit equivalent is that of figure 7-4, and its driving voltage U is equal to Es (step voltage).  For the three  examples of a hand-to-both-feet contact figure 7-1 applies, and U is equal to Et (touch voltage), Em (mesh voltage), or Etrrd (transferred voltage), respectively.  The accidental circuit involving metal-to-metal contact, either hand-to-hand or hand-to-feet, is shown in figure 8-3 where U is equal to the metal-to-metal touch voltage, Emm .

Figure 8-1 {old fig 9}
Figure 8-1

Basic shock situations

Figure 8-2 {old fig 10}
Figure 8-2

Typical situation of extended transferred potential

During a fault, the earth conducts currents emanating from the grid and other permanent ground electrodes buried below the earth surface.  The resulting potential gradients have a primary effect on the value of U.

In the case of conventional substations, the typical case of metal-to-metal touch voltage occurs when metallic objects or structures within the substation site are not bonded to the ground grid.  Objects such as pipes, rails or fences not bonded to the ground grid that are located within or near the substation ground grid area meet this criteria.  Substational metal-to-metal touch voltages may be present when a person standing on or touching a grounded object or structure and comes into contact with a metallic object or structure within the substation site that is not bonded to the ground grid.  Calculation of the actual metal-to-metal touch voltage is complex.  In practice, hazards resulting from metal-to-metal contact may best be avoided by bonding potential danger points to the substation grid.

Typically, the case of transferred voltage occurs when a person standing within the substation area touches a conductor grounded at a remote point, or a person standing at a remote point touches a conductor connected to the substation grounding grid.  During fault conditions, the resulting potential to ground may equal or exceed the full GPR of a grounding grid discharging the fault current, rather than the fraction of this total voltage encountered in the ordinary touch contact situations (see figure 8-2).  In fact, as discussed in clause 17, the transferred voltage may exceed the sum of the GPR's of both substations, due to induced voltages on communication circuits, static or neutral wires, pipes, etc.  It is impractical, and often impossible, to design a ground grid based on the touch voltage caused by the external transferred voltages.  Hazards from these external transferred voltages are best avoided by using isolating or neutralizing devices and by treating and clearly labeling these circuits, pipes, etc., as being equivalent to live lines.

8.3  Step and touch voltage criteria

The safety of a person depends on preventing the critical amount of shock energy from being absorbed before the fault is cleared and the system de-energized.  The maximum driving voltage of any accidental circuit should not exceed the limits defined below. For step voltage the limit is





(29)

Combining equation (29) with equations (10), (18), (21) and either (8) or (9), and letting b= 0.08m





(30a)





(30b)

Similarly, the touch voltage limit is





(31)

Combining equation (31) with equations (10), (15), (21) and either (8) or (9), and letting b=0.08m





(32a)





(32b)

where


Cs 
is determined from figure 7-6


(s  
is the resistivity of the surface material in (-m


ts  
is the duration of shock current in seconds

If no protective surface layer is used, then Cs  =1 and (s = (.

The metal-to-metal touch voltage limits are derived from the touch voltage equations, equations (32a) and (32b).  Metal-to-metal contact, both hand-to-hand and hand-to-feet, will result in a (s = 0.  Therefore, the total resistance of the accidental circuit is equal to the body resistance, RB .

With the substitution of (s  = 0 in the foot resistance terms of equations (32a) and (32b), the metal-to-metal touch voltage limit is:




SEC Equation  \*   \h
(33)




SEC Equation  \*   \h
(34)

The actual step voltage, touch voltage, or metal-to-metal touch voltage should be less than the respective maximum allowable voltage limits to ensure safety.  Hazards from external transferred voltages are best avoided by isolation or neutralizing devices and labeling these danger points as being equivalent to live lines.

8.4  Typical shock situations for gas-insulated substations

In the grounding analysis of gas-insulated substations (GIS), the touch voltage considerations present several unique problems.  Unlike conventional facilities, the GIS equipment features a metal sheath enclosing gas-insulated switchgear and inner high-voltage buses.  Each bus is completely contained within its enclosure and the enclosures are grounded.  Because a voltage is induced in the outer sheath whenever a current flows in the coaxial busbar, certain parts of the enclosure might be at different potentials with respect to the substation ground.  To evaluate the maximum voltage occurring on the bus enclosure during a fault, it is necessary to determine the inductance of the outer sheath to ground, the inductance of the inner conductor, and the mutual inductances for a given phase configuration of individual buses.

A person touching the outer sheath of GIS might be exposed to voltages resulting from two basic fault conditions:

a) An internal fault within the gas-insulated bus system, such as a flashover between the bus conductor and the inner wall of the enclosure.

b) A fault external to the GIS in which a fault current flows through the GIS bus and induces currents in the enclosures.

Because the person may stand on a grounded metal grating and the accidental circuit may involve a hand-to-hand and hand-to-feet current path, the analysis of GIS grounding necessitates consideration of metal-to-metal touch voltage; figure 8-3.

Figure 8-3 {old fig 11 or new}

Figure 8-3

Typical metal-to-metal touch situations in GIS
Most GIS manufacturers consider the enclosure properly designed and adequately grounded if the potential difference between individual enclosures, and the potential difference between an enclosure and other grounded structures, does not exceed 65-130 V during a fault.  The metal-to-metal touch voltage equations, equations (33) and (34), reveals that this voltage range corresponds to fault times ranging from 0.8 to 3.2 s if a 50 kg criterion is used, and ranging from 1.46 to 5.8 s for the assumption of a 70 kg body.  This relationship is, however, better perceived in the graphical form of figure 8-4, which also helps to grasp the related problem of sufficient safety margins.

Figure 8-4 {old fig 12}

Figure 8-4

Touch voltage limits for metal-to-metal contact and a typical range of enclosure voltages to ground
The fault conditions and the corresponding circuit equivalents for determining or verifying the critical safety design parameters of GIS grounding will be discussed in more detail in clause 10.

8.5  Effect of sustained ground currents

After the safe step and touch voltage limits are established, the grounding system can then be designed based on the available fault current and overall clearing time.  The designer should also consider sustained low-level (below setting of protective relays) fault magnitudes that may be above the let-go current threshold.  Some sustained faults above the let-go current, but below the fibrillation threshold, may cause asphyxiation from prolonged contraction of the chest muscles.  However, it would not be practical to design against lesser shocks that are painful, but cause no permanent injury.

9.  Principal design considerations
9.1  Definitions

9.1.1  auxiliary ground electrode:  A ground electrode with certain design or operating constraints.  Its primary function maybe other than conducting the ground fault current into the earth.

9.1.2  ground electrode:  A conductor imbedded in the earth and used for collecting ground current from or dissipating ground current into the earth.

9.1.3  ground mat:  A solid metallic plate or a system of closely spaced bare conductors that are connected to and often placed in shallow depths above a ground grid or elsewhere at the earth surface, in order to obtain an extra protective measure minimizing the danger of the exposure to high step or touch voltages in a critical operating area or places that are frequently used by people.  Grounded metal gratings, placed on or above the soil surface or wire mesh placed directly under the surface material, are common forms of a ground mat.

9.1.4  grounding grid:  A system of horizontal ground electrodes that consists of a number of interconnected, bare conductors buried in the earth, providing a common ground for electrical devices or metallic structures, usually in one specific location.

NOTE: Grids buried horizontally near the earth's surface are also effective in controlling the surface from potential gradients.  A typical grid usually is supplemented by a number of ground rods and may further connected to auxiliary ground electrodes, to lower its resistance with respect to remote earth.

9.1.5  grounding system:  Comprises all interconnected grounding facilities in a specific area.

9.1.6  primary ground electrode:  A ground electrode specifically designed or adapted for discharging the ground fault current into the ground, often in a specific discharge pattern, as required (or implicitly called for) by the grounding system design.

9.2
  General concept

A grounding system should be installed in a manner that will limit the effect of ground potential gradients to such voltage and current levels that will not endanger the safety of people or equipment under normal and fault conditions, as well as assure continuity of service.

In the discussion that follows, it is assumed that the system of ground electrodes has the form of a grid of horizontally buried conductors, supplemented by a number of vertical ground rods connected to the grid.  Based on two surveys, the first reported in an AIEE application guide in 1954 [B1], and the second published in 1980 [B40], this concept represents the prevailing practice of most utilities both in the USA and in other countries.

Some of the reasons for using the combined system of vertical rods and horizontal conductors are as follows:

a) In substations a single electrode is, by itself, inadequate in providing a safe grounding system.  In turn, when several electrodes, such as ground rods, are connected to each other and to all equipment neutrals, frames, and structures that are to be grounded, the result is, essentially, a grid arrangement of ground electrodes, regardless of the original objective.  If the connecting links happen to be buried in a soil of good conductivity, this network alone may represent an excellent grounding system.  Partly for this reason, some utilities depend on the use of a grid alone. However, ground rods are of a particular value, as explained next.

b) If the magnitude of current dissipated into the earth is high, it seldom is possible to install a grid with resistance so low as to assure that the rise of a ground potential will not generate surface gradients unsafe for human contact.  Then, the hazard can be eliminated only by control of local potentials through the entire area.  A system that combines a horizontal grid and a number of vertical ground rods penetrating lower soils has the following advantages:

1) While horizontal (grid) conductors are most effective in reducing the danger of high step and touch voltages on the earth's surface, provided that the grid is installed in a shallow depth usually 0.3‑0.5m (12‑18 in) below grade, sufficiently long ground rods will stabilize the performance of such a combined system.  For many installations this is important because of freezing or drying of upper soil layers could vary the soil resistivity with seasons, while the resistivity of lower soil layers remains nearly constant.

2) Rods penetrating the lower resistivity soil are far more effective in dissipating fault currents whenever a two‑ or multilayer soil is encountered and the upper soil layer has higher resistivity than the lower layers.  For many gas-insulated substations (GIS) and other space‑limited installations, this condition becomes in fact the most desirable one to occur, or to be achieved by the appropriate design means (extra long ground rods, grounding wells, etc.).

3) If the rods are installed predominately along the grid perimeter in high-to-low or uniform soil conditions, the rods will considerably moderate the steep increase of the surface gradient near the peripheral meshes.  Specific details of this arrangement will be further discussed in clause 16.  These details are pertinent to the use of simplified methods in determining the voltage gradient at the earth's surface.

9.3  Primary and auxiliary ground electrodes

In general, most grounding systems utilize two groups of ground electrodes.  Primary ground electrodes are specifically designed for grounding purposes.  Auxiliary ground electrodes are electrodes that comprise various underground metal structures installed for purposes other than grounding. Typical primary electrodes include such things as grounding grids, counterpoise conductors, ground rods, and wells.  Typical auxiliary electrodes include underground metal structures and reinforcing bars encased in concrete, if connected to the grounding grid.  Auxiliary ground electrodes may have a limited current carrying capability.

9.4  Basic aspects of grid design

Conceptual analysis of a grid system usually starts with inspection of the substation layout plan, showing all major equipment and structures.  In order to establish the basic ideas and concepts, the following points may serve as guidelines for starting a typical grounding grid design:

a) A continuous conductor loop should surround the perimeter to enclose as much area as practical.  This measure helps to avoid high current concentration and hence high gradients both in the grid area and near the projecting cable ends.  Enclosing more area also reduces the resistance of the grounding grid.

b) Within the loop, conductors are typically laid in parallel lines and, where practical, along the structures or rows of equipment, to provide for short ground connections

c) A typical grid system for a substation may include 4/0 bare copper conductors buried 0.3 ‑ 0.5 m (12 ‑ 18 in) below grade, spaced 3 ‑ 7 m (10 ‑ 20 ft) apart, in a grid pattern.  At cross‑connections, the conductors would be securely bonded together. Ground rods may be at the grid corners and at junction points along the perimeter.  Ground rods may also be installed at major equipment, especially near surge arresters.  In multilayer or very resistive soils, it might be useful to use longer rods or rods installed at additional junction points.

d) This grid system would be extended over the entire substation switchyard and often beyond the fence line.  Multiple ground leads or larger sized conductors would be used where high concentrations of current may occur, such as at a neutral‑to‑ground connection of generators, capacitor banks, or transformers.

e) The ratio of the sides of the grid meshes usually is from 1:1 to 1:3, unless a precise (computer‑aided) analysis warrants more extreme values.  Frequent cross‑connections have a relatively small effect on lowering the resistance of a grid.  Their primary role is to assure adequate control of the surface potentials.  The cross-connections are also useful in securing multiple paths for the fault current, minimizing the voltage drop in the grid itself, and providing a certain measure of redundancy in the case of a conductor failure.

9.5
  Design in difficult conditions

In areas where the soil resistivity is rather high or the substation space is at a premium, it may not be possible to obtain a low impedance grounding system by spreading the grid electrodes over a large area, as is done in more favorable conditions.  Such a situation is typical of many GIS installations and industrial customer’s substations, occupying only a fraction of the land area normally used for conventional equipment.  This often makes the control of surface gradients difficult. Some of the solutions include:

a) Connection(s) of remote ground grid(s) and adjacent grounding facilities; a combined system utilizing separate installations in buildings, underground vaults, etc.  A predominant use of remote ground electrodes requires careful consideration of transferred potentials, surge arrester locations, and other critical points.  A significant voltage drop may develop between the local and remote grounding facilities, especially for high-frequency surges (lightning).
b) Use of deep-driven ground rods and drilled ground wells.

c) Various additives and soil treatments used in conjunction with ground rods and interconnecting conductors are more fully described in 14.5.

d) Use of wire mats.  It is feasible to combine both a surface material and fabricated mats made of wire mesh to equalize the gradient field near the surface.  A typical wire mat might consist of copper‑clad steel wires of No 6 AWG, arranged in a 0.6 x 0.6 m (24 x 24 in) grid pattern, installed on the earth's surface and below the surface material, and overlaying the main grounding grid, which is installed in greater depth, usually between 0.3 to 0.5 m (12 to 18 in).

e) Where feasible, controlled use of other available means to lower the overall resistance of a ground system, such as connecting static wires and neutrals to the ground (see 15.3). Typical is the use of metallic objects on the site that qualify for and can serve as auxiliary ground electrodes, or as ground ties to other systems. Consequences of such applications, of course, have to be carefully evaluated.

f) Wherever practical, a nearby deposit of low resistivity material of sufficient volume can be used to install an extra (satellite) grid.  This satellite grid, when sufficiently connected to the main grid, will lower the overall resistance and, thus, the ground potential rise of the grounding grid.  The nearby low resistivity material may be a clay deposit or it may be a part of some large structure, such as the concrete mass of a hydroelectric dam. [B146]

9.6
  Connections to grid

Conductors of adequate ampacity and mechanical strength (see clause 11) should be used for the connections between:

a) All ground electrodes, such as grounding grids, rodbeds, ground wells, and, where applicable, metal, water, or gas pipes, water well casings, etc.

b) All above‑ground conductive metal parts that might accidentally become energized, such as metal structures, machine frames, metal housings of conventional or gas‑insulated switchgear, transformer tanks, guards, etc.  Also, conductive metal parts that might be at a different potential relative to other metal parts that have become energized should be bonded together, usually via the ground grid.

c) All fault current sources such as surge arresters, capacitor banks or coupling capacitors, transformers, and, where appropriate, machine neutrals, lighting and power circuits.

Copper cables or straps are usually employed for these ground connections.  However, transformer tanks are sometimes used as part of a ground path for surge arresters thereon.  Similarly, most steel or aluminum structures may be used for the ground path if it can be established that their conductance, including that of any connections, is and can be maintained as equivalent to that of the conductor that would normally be installed.  Where this practice is followed, any paint films that might otherwise introduce a highly resistive connection should be removed and a suitable joint compound applied or other effective means, such as jumpers across the connections, taken to prevent subsequent deterioration of the connection.  In the case of GIS installations, extra attention should be paid to the possibility of unwanted circulation of induced currents.  Clause 10 covers the subject in more detail.

Equal division of currents between multiple ground leads at cross‑connections or similar junction points should not be assumed.

All accessible ground leads should be inspected on a periodic basis.  Exothermic weld, brazed, or pressure type connectors can be used for underground connections (see 11.6).  Soldered connections should be avoided because of the possibility of failure under high fault currents.

Open circuits, even in exposed locations, can escape detection, and it obviously is impractical to inspect buried portions of the grounding network once it is installed.  More detailed discussion of test methods used to determine the continuity of buried grounding systems is included in 19.4.  (make sure this is added to 19.4???) Those facilities that are most likely to supply or carry a high current, such as transformer and circuit breaker tanks, switch frames, and arrester pads, should always be connected to the grid with more than one ground lead.  The leads should preferably be run in opposite directions to eliminate common mode failure.

note:  some references here refer to the 4 new ones at the end of this clause - need to be incorporated ???

10.  Special considerations for gas‑insulated substations (GIS)

10.1  Definitions

10.1.1  continuous enclosure:  A bus enclosure in which the consecutive sections of the housing along the same phase conductor are bonded together to provide an electrically continuous current path throughout the entire enclosure length.  Cross-bondings, connecting the other phase enclosures, are made only at the extremities of the installation and at a few selected intermediate points.

10.1.2  enclosure currents:  Currents that result from the voltages induced in the metallic enclosure by the current(s) flowing in the enclosed conductor(s).

10.1.3  gas-insulated substation:  A compact, multicomponent assembly, enclosed in a grounded metallic housing in which the primary insulating medium is a com​pressed gas, and that normally consists of buses, switchgear, and associated equipment (subassemblies).

10.1.4  main ground bus:  A conductor or system of conductors provided for connecting all designated metallic components of the GIS to a substation grounding system.

10.1.5  noncontinuous enclosure:  A bus enclosure with the consecutive sections of the housing of the same phase conductor electrically isolated (or insulated from each other), so that no current can flow beyond each enclosure section.

10.1.6  transient  enclosure voltage (TEV):  Very fast transient phenomena, which are found on the grounded enclosure of GIS systems.  Typically, ground leads are too long (inductive) at the frequencies of interest to effectively prevent the occurrence of TEV.  The phenomenon is also known as transient ground rise (TGR) or transient ground potential rise (TGPR). [1???], [2???]

10.1.7  very fast transient (VFT):  A class of transients generated internally within GIS characterized by short duration and very high frequency nature [1].  VFT is generated by the rapid collapse of voltage during breakdown of the SF6 insulating gas, either across the contacts of a switching device or line-to-ground during a fault.  These transients can have rise times in the order of nanoseconds implying a frequency content extending to about 100 MHz.  However, dominant oscillation frequencies, which are related to physical lengths of GIS bus are usually in the 20-40 Mhz range. 

10.1.8  very fast transients overvoltage (VFTO):  System overvoltages which result from generation of VFT.  While VFT are one of the main constituents of VFTO, some lower frequency (( 1 MHz) component may be present as a result of the discharge of lumped capacitance (PTs, CVTs, etc.).  Typically, VFTO will not exceed 2.0 per unit although higher magnitudes are possible in specific instances. [1???]

10.2  GIS characteristics

Gas‑insulated substations (GIS) are subjected to the same magnitude of ground fault current and require the same low impedance grounding as conventional substations.

Typically, the GIS installation necessitates 10 ‑ 25% of the land area required for conventional equipment.  Because of this smaller area it may be difficult to obtain adequate grounding solely by conventional methods.  Particular attention should be given to the bonding of the metallic enclosures of the GIS assembly, as these enclosures carry induced currents of significant magnitude, which must be con​fined to specific paths.  In this respect, grounding recommendations by the manufacturer of a given GIS usually need to be strictly followed.

As a result of the compact nature of GIS and its short distances, electrical breakdown in the SF6 gas, either across the contacts of a switching device during operation or in a fault generates very high frequency transients which can couple onto the grounding system.  In some cases, these transients may have to be considered in the overall grounding design.  These transients may cause high magnitude short duration ground rises and are also the source of electromagnetic interference (EMI) in the GIS.  While EMI is beyond the scope of this document, the EMI mitigation techniques often involve special considerations in the grounding design. [???3]

10.3  Enclosures and circulating currents

The shielding effectiveness of the bus enclosure is determined by its impedance, which governs the circulation of induced currents.

With separate enclosures for each phase, the magnitude and direction of the enclosure current is influenced by the size of the enclosure and the phase spacing between the buses, as well as by the method of interconnecting the enclosures.

In a continuous enclosure design, a voltage is induced in an enclosure by the current in the conductor that it surrounds, producing a longitudinal current flow in the enclosure.  When a continuity of all phase enclosures is maintained through short connections at both ends, the enclosure current is only slightly less than that flowing in the inner bus in the opposite direction.  This current returns through the housing (enclosures) of adjacent phases when the load is equalized between phases.  The magnetizing current lags the enclosure current by approxi​mately 90 degrees.  The flux is mainly contained within the enclosure.

In a noncontinuous enclosure design, there are no external return paths for enclosure currents.  Thus the voltage induced in a noncontinuous enclosure by the current of an inner bus(es) that it surrounds cannot produce any longitudinal current flow.  Also, voltages might be induced in each enclosure by the currents in the conductors not enclosed by it.  Nonuniform voltages result, causing local current flows in each isolated enclosure section, with the currents flowing in nonuniform patterns.  Because of these properties, the noncontinuous design is generally considered less advantageous than that of the continuous type.  As such, it is not currently used by the industry.

10.4  Grounding of enclosures

Normally, the continuous type enclosures provide a return path for induced currents so that the conductor and enclosure form a concentric pair with effective external shielding of the field internal to the enclosure.  However, under asymmetrical faults, the dc component is not shielded and causes an external voltage drop due to enclosure resistance.

Frequent bonding and grounding of GIS enclosures is the best solution to minimize hazardous touch and step voltages within the GIS area.  Additional measures
 include the use of conductive platforms (ground mats) that are connected to GIS structures and grounded.  Servicing platforms usually are an integral part of the GIS design supplied by the manufacturer.

To limit the undesirable effects caused by circulating currents, the following requirements should be met:

a) All metallic enclosures should normally operate at ground voltage level.

b) When grounded at the designated points, the bus enclosure design should ensure that no significant voltage differences exist between individual enclosure sections and that neither the supporting structures nor any part of the grounding systems is adversely influenced by the flow of induced currents.

c) To avoid the circulation of enclosure currents beyond regular return path within the GIS assembly, power cable sheath grounds should be tied to the grounding system via connections that are separated from the GIS enclosures.  To facilitate this isolation, the design of cable terminations  should be such that an isolating air gap or proper insulation elements are provided.  Very fast transients generated by switching or by faults in the GIS may cause these insulation elements to flashover.  In such cases, the consequences of such flashovers on current distribution within the grounding system should be considered. [???4]

d) Enclosure return currents also cannot be permitted to flow through any mounted current transformers. 

10.5  Cooperation between GIS manufacturer and user

Usually it is the GIS manufacturer who defines clearly what constitutes the main ground bus of the GIS and specifies what is required of the user for connecting the GIS assembly to the substation ground.  Ample documentation is necessary to assure that none of the proposed connections from the main ground bus to the grounding grid will interfere with the required enclosure current path or any other operational feature of the GIS design. That may be especially pertinent if the main ground bus consists of a system of interconnections between the GIS components and structures, and no separate busbar (continuous common ground bus loop) is furnished.

Usually the GIS manufacturer also provides, or is responsible for:

a) Providing the subassembly-to-subassembly bonding to assure safe voltage gradients between all intentionally grounded parts of the GIS assembly and between those parts and the main ground bus of the GIS.

b) Furnishing readily accessible connectors of sufficient mechanical strength to withstand electromagnetic forces and normal abuse, and that are capable of carrying the anticipated maximum fault current in that portion of the circuit without overheating.

c) Providing ground pads or connectors, or both, allowing, at least, for two paths to ground from the main ground bus, or from each metallic enclosure and auxiliary piece of GIS equipment designated for a connection to the substation ground if the main ground bus of the GIS assembly does not actually exist.

d) Recommending proper procedures for connections between dissimilar metals, typically between a copper cable or a similar ground conductor and aluminum enclosures.

The user usually provides information on the sources of fault current and the expected magnitudes and durations that should be considered.  Moreover, the user should assist the GIS manufacturer in reviewing all proposed grounding provisions in order to assure proper interfacing of:

a) Connections for the neutral current of grounded equipment or apparatus and for dissipating surges caused by lightning and switching within the GIS.

b) Devices for dissipating lightning and switching surge currents external to the GIS assembly.

c) Requirements of protective relaying, and satisfying the provisions necessary for telephone and communication facilities.

d) Ground connections to all GIS supporting frames and structures, metallic sheaths, and installation of shielding for cable terminations where applicable. 

e) Connections to all pads or connectors furnished by the GIS manufacturer.

f) Safe voltage for step and touch, under both normal and abnormal operating conditions external to the GIS assembly.

g) Compliance with the grounding specifications, related to correct grounding practices, as mutually agreed to by the GIS manufacturer and the user.

10.6  Other special aspects of GIS grounding

Precautions should be undertaken to prevent excessive currents from being induced into adjacent frames, structures, or reinforcing steel, and to avoid establishment of current loops via other substation equipment, such as transformers or separate switchgear.  If there is the possibility of undesirable current loops via ground connections, or if any sustained current path might partially close or pass through grounded structures, the substation grounding scheme and the physical layout should be carefully reviewed with the GIS manufacturer.

Equal care is needed in the proximity of discontinuities in enclosure grounding paths at the transformer connections to GIS and at the interface points to conventional switchgear to prevent circulating currents in the circuit breaker and transformer tank steel.

Where applicable, all isolating elements should be able to withstand the full potential difference that may occur between the locally grounded system and that external to the GIS.  In many cases, the very fast transients generated by switching or by faults in GIS may cause very high transient voltages to appear at these points.  For instance, the isolation of high‑pressure oil pipe cables from the GIS grounding system often involves difficulties.  Although the individual HV or EHV terminators may provide adequate separation from the external grounds ‑ by the virtue of a design that usually includes the use of base plate insulators made of high voltage rated porcelain or fiberglass, problems sometimes arise if the same level of insulation is also expected at other interface points.  One typical problem area is the auxiliary piping between the oil chamber of individual GIS terminators and the oil diffusion chamber at the end of a pipe cable that fre​quently branches to a variety of oil pressure monitoring instruments and alarm devices [B72].  There the isolation of metal parts is often achieved by the means of ceramic or plastic inserts.  Adequate creepage distance should be ensured where possible.  To protect against transient voltages, other precautions might be necessary. [B ???]

In these and similar circumstances,
 a close cooperation with the GIS manufacturer in the early stages of the design is very important.

10.7  Notes on grounding of GIS foundations

Since the earth path of ground currents is strongly affected by the relative position of conductive objects that are in the ground, more attention should be paid to those portions of the GIS ground​ing system that include discontinuities, or where the design requires an abrupt change in the pattern of ground electrodes.  The following circumstances are of concern.

In the limited space of GIS substations, a substantial part of the substation area is often occupied by concrete foundations, which may cause irregularities in a current discharge path.  In this respect, a simple monolithic concrete steel reinforced slab is advantageous both as an auxiliary grounding device and for seismic reasons.

If a continuous floor slab is used, a good adjunct measure is to tie its reinforcing steel mesh to the common ground bus (main ground bus) so that both the GIS enclosures and the structural steel in and above the foundation will be approximately the same potential level.  The assumption is that this measure should produce a better ground and the reinforcing bars, being considerably closer together than the wires of a typical ground grid, should produce more even potentials within the floor and at the surface.

The reinforcing bars and other metal in GIS foundations can act as auxiliary ground electrodes and may be so used provided that under no circumstances the discharge of current would result in a damage of concrete because of local overheating or a gradual erosion of the concrete‑steel bonds.  For further details, refer to 14.6.

10.8  Touch voltage criteria for GIS

Although the GIS manufacturer generally designs the equipment to meet the already mentioned requirements for safe operation and usually performs most, if not all, calculations that are necessary for determining the sheath voltages and currents during faults, there still are circumstances when the user has to ascertain that the entire installation is safe.  Having this possibility in mind, some of the critical aspects of interconnecting the GIS with a grounding system are briefly discussed next.

A certain paradox, inherent to the GIS design, may occur when one tries to determine the best concept of GIS grounding.  In contrast to the general wisdom that a large ground connection necessarily equals a good grounding practice, the circulating currents generated in the GIS enclosures during a fault should also be taken into account.  To be considered are: (1) where these currents will circulate and (2) where and to what degree the design engineer or GIS manufacturer, or both, prefer these currents to circulate.

Typically in a continuous enclosure design, the path of enclosure currents includes some structural members of the GIS frame and the enclosures themselves.  With each phase enclosure tied to the enclosures of adjacent phases at both ends, several loops are formed.  Because a cross section of the mentioned structural members is usually much smaller than that of the enclosure and comparable to that of the grounding straps that connect the GIS assembly to a ground grid (and for that matter, also to the reinforcing bars of the concrete foundation),several questions need to be asked:

a) If the currents divide and flow via all available metallic paths, what ratio is to be expected between the currents circulating within the GIS assembly and those circulating via a ground connection?

b) How much current circulating via a ground connection loop is too much?

c) Should the GIS be designed to be safe if no circulating current would (at least for an external fault) circulate via ground connections?

d) And finally, how much grounding is needed for the best balance between operational and safety‑related requirements?

Presently, there are no clear‑cut answers and solutions to the above questions. Some manufacturers prefer to supply a special ground bus (main ground bus) as a part of the GIS package, with clearly designated ground connection points.  Others do not use any main ground bus at all, but simply designate certain points on the enclosure as grounding pads and let the utility complete the grounding.

In either case, it becomes necessary to limit the body current to some value in a milliampere range, while the fault currents that are of concern range from hundreds to thousands of amperes.  Thus, one can safely assume that the full potential difference existing prior to a contact would not change while forcing the current through an alternate path including the body.  Then the case of a person touching the GIS sheath metal can be reduced to the problem of finding the voltage drop between two points of contact along one or between two enclosures and a common ground.  For the hand‑to‑feet contact made by a person standing on a nonmetallic surface (concrete slab or soil layer above the grounding grid, etc.), only a minor modification of the application criterion of equations (32a) and (32b) is required in order to take into account the maximum inductive voltage drop occurring within the GIS assembly.

The touch voltage criterion for GIS is:





(35)

where


Et 
is the maximum touch voltage, as determined for the point underneath a person's feet


E'to max
is the (predominantly inductive) maximum value of metal‑to‑metal voltage difference on and between GIS enclosures, or between these enclosures and the supporting structures, including any horizontal or vertical members for which the GIS assembly is designed

In practical situations, as shown in figure 10-1, a multiplicity of return paths and considerable cross‑coupling occurs.  This makes the calculation of longitudinally induced currents difficult and for some remote external faults often outright unpractical, as too many parameters remain undefined.  As a rule, because of a great variety in possible physical arrangements of the GIS assembly, the GIS manufacturers do detail calculations for determining the basic design parameters, such as spacing and location of bonds, etc.

FIGURE 10-1 {old fig 13}
Figure 10-1

Typical faults in GIS
10.9  Recommendations

a) When applying the touch voltage criterion equation (35), the following facts should be considered.  The case of an internal fault with ground return requires the addition of the resistive and inductive voltage drop to the resistive drop repre​senting the difference of potentials between the substation ground and the point beneath a person's feet.  This generally is not necessary for faults external to the GIS.  For an external line‑to‑ground fault, the voltages induced on the sheath should be checked for a hand‑to‑hand metal‑to‑metal contact, but the calculation of step and touch voltages at the earth's surface is the same as that for conventional installations (i.e., the inductive term E’to max in equation (35) is zero).

b) In evaluating the magnitude of induced voltages caused by faults external to the GIS, only the case of a close-in fault [case (B) in figure 10-1] needs to be analyzed because remote external faults will cause less of a problem.

References

1) CIGRE Working Group 33/13-09  “Very Fast Phenomena Associated with Gas-Insulated Substations.”  1988 Session of CIGRE, paper 33-13.

2) Fijimoto, N., E.P. Dick, S.A. Boggs and G.L. Ford. “Transient Ground Potential Rise in Gas-Insulated Substations - Experimental Studies.”  IEEE Trans. on PAS, PAS101, No. 10, October 1982.

3) Harvey, S.M.  “Control Wiring Transients and Electromagnetic Compatibility in GIS.”  In S.A. Boggs, F.Y. Chu and N. Fujimoto (Eds) “Gas-Insulated Substations - Technology & Practice,”  Pergamon Press, New York 1986.

4) Fujimoto, N., S.J. Croall and S.M. Foty,  “Techniques for the Protection of Gas-Insulated Substation to Cable Interfaces.”  IEEE Transactions on Power Delivery, volume 3, Number 4, October 1988.
11.  Selection of conductors and connections

In assessing which conductor material and what conductor size or what maximum allowable temperature limit need to be applied in individual design situations, the final choice should always reflect the considerations outlined below.

11.1  Basic requirements

Each element of the grounding system, including grid conductors, connections, connecting leads, and all primary electrodes, should be so designed that for the expected design life of the installation, the element will:

a) Have sufficient conductivity, so that it will not contribute substantially to local voltage differences.

b) Resist fusing and mechanical deterioration under the most adverse combination of a fault magnitude and duration.

c) Be mechanically reliable and rugged to a high degree.
d) Be able to maintain its function even when exposed to corrosion or physical abuse.

The first requirement for selecting a conductor with sufficient conductivity is usually fulfilled when the other three  requirements are satisfied.

11.2  Choice of material for conductors and related corrosion problems
11.2.1  Copper conductor

Copper is a common material used for grounding. Copper conductors, in addition to their high conductivity, have the advantage of being resistant to most underground corrosion because copper is cathodic with respect to most other metals that are likely to be buried in the vicinity. 

11.2.2  Copper-clad steel

Copper-clad steel is usually used for underground rods and occasionally for grounding grids, especially where theft is a problem. Use of copper, or to a lesser degree copper-clad steel, therefore assures that the integrity of an underground network will be maintained for years, so long as the conductors are of an adequate size and not damaged and the soil conditions are not corrosive to the material used.

Nevertheless, because a grid of copper or copper-clad steel forms a galvanic cell with buried steel structures, pipes and any of the lead-based alloys that might be present in cable sheaths, it is also likely to hasten corrosion of the latter.  Tinning the copper has been tried by some of the utilities.  That reduces the cell potential with respect to steel and zinc by about 50 percent and practically eliminates this potential with respect to lead (tin being slightly sacrificial to lead).  The disadvantage of using tinned copper conductor is that it accelerates and concentrates the natural corrosion, caused by the chemicals in the soil, of the copper in any small bare area. Other often used methods are:

a) Insulation of the sacrificial metal surfaces with a coating such as plastic tape, asphalt compound, or both.

b) Routing of buried metal elements so that any copper-based conductor will cross water pipe lines or similar objects made of other uncoated metals as nearly as possible at right angles, and then applying an insulated coating to one metal or the other where they are in proximity. The insulated coating is usually applied to the pipe.

c) Cathodic protection using sacrificial anodes or impressed current systems.

d) Use of nonmetallic pipes and conduit.

11.2.3  Aluminum

Aluminum has been used for ground grids less frequently. Though at first glance the use of aluminum would be a natural choice for equipment in gas insulated substations (GIS) because the enclosures are made of aluminum or aluminum alloys, there are several disadvantages to consider:

a) Aluminum itself may corrode in certain soils. The layer of corroded aluminum material is nonconductive for all practical grounding purposes.

b) Gradual corrosion caused by alternating currents may also be a problem under certain conditions.

Thus, aluminum should be used only after full investigation of all circumstances, despite the fact that, like steel, it would alleviate the problem of contributing to the corrosion of other buried objects.  However, it is anodic to many other metals, including steel and, if interconnected to one of these metals in the presence of an electrolyte, the aluminum will sacrifice itself to protect the other metal. If aluminum is used, the high purity electric conductor grades are recommended as being more suitable than most alloys.

11.2.4  Steel conductor

Steel has been used for ground grid conductors, mainly due to the benefit of eliminating most of the adverse effects of copper already mentioned. Of course, such a design requires that attention is paid to the grid itself.  Use of a galvanized or corrosion resistant steel, in combination with cathodic protection, is typical. [B91]

11.2.5  Other considerations

In GIS, the use of cathodic protection may also be required for other reasons. Common is the protection of facilities that are external to the GIS, such as pressurized pipe-type cables, lead shielded cables, etc.  Because of the complexity of GIS installations, it is essential to consider all aspects of corrosion prevention before designing the grounding system. Specific guidelines are difficult to establish because substation conditions may be different due to location and application in the electric power system.

The subject of underground corrosion and cathodic protection is complex. Many studies have been made and much has been published on this subject. A detailed discussion of these phenomena is beyond the scope of this guide.

11.3  Conductor sizing factors

11.3.1  Symmetrical currents
The short time temperature rise in a ground conductor, or the required conductor size as a function of conductor current, can be obtained from equations (36) through (41), which are taken from the derivation by Sverak [B132] and is also included as Appendix B in IEEE Std 837.  These equations evaluates the ampacity of any conductor  for which the material constants are known, or can be determined by calculation.  Material constants of the commonly used grounding materials are listed in table 11-1.   Equations (36) through (41) are derived for symmetrical currents (with no dc offset).






(36)

where
I
is the rms current in kA

Amm2
is the conductor cross section in mm2
Tm
is the maximum allowable temperature in oC
Ta

is the ambient temperature inoC
Tr

is the reference temperature for material constants in oC
(o

is the thermal coefficient of resistivity at 0oC in 1/oC
(r

isthe thermal coefficient of resistivity at reference temperature Tr in 1/oC
(r

is the resistivity of the ground conductor at reference temperature Tr in



((-cm

Ko

1/(o or (1/(r) - Tr inoC
tc

is the duration  of current in s 

TCAP 
is the thermal capacity per unit volume from table 11-1, in J/(cm3·oC) (further defined in 11.3.1.1)

Note that (r and (r are both to be found at the same reference temperature of Tr degrees Celsius. Table   11-1 provides data for (r and (r at 20oC.

If the conductor size is given in kcmils (mm2 X 1.974 = kcmils), equation  (36) becomes






(37)
Table 11-1

Material constants
Description
Material

Conductivity

(%)
(r
Factor

@ 20°C
Ko
(1/(o)

@ 0°C
Fusinga
temperature

Tm(°C)
(r
@ 20 °C

(µ(-cm)


TCAP Thermal capacity 

[J/(cm3 . (C)]

Copper, annealed soft-drawn

100.0
0.003 93

234

1083

1.72

3.42

Copper, commercia hard-drawn

97.0
0.003 81

242

1084

1.78

3.42

Copper-clad steel core wire

40.0
0.003 78

245

1084

4.40

3.85

Copper-clad steel core wire

30.0
0.003 78

245

1084

5.86

3.85

Copper-clad steel core rodb

20.0
0.003 78

245

1084

8.62

3.85

Aluminum, EC grade

61.0
0.004 03

228

657

2.86

2.56

Aluminum, 5005 alloy

53.5
0.003 53

263

652

3.22

2.60

Aluminum, 6201 alloy

52.5
0.003 47

268

654

3.28

2.60

Aluminum-clad steel core

20.3
0.003 60

258

657

8.48

2.67

Steel, 1020

10.8
0.001 60

605

1510

15.90

3.28

Stainless-clad steel core rodc

9.8
0.001 60

605

1400

17.50

4.44

Zinc-coated steel core

8.6
0.003 20

293

419

20.10

3.93

Stainless steel, 304

2.4
0.001 30

749

1400

72.00

4.03

aFrom ASTM standards

bCopper-clad steel rod based on 0.010 in (0.254 mm) copper thickness.

cStainless-clad steel rod based on 0.020 in (0.508 mm) No. 304 stainless steel thickness over No. 1020 steel core.

Equations (36) and (37), in conjunction with equation (38) (which defines TCAP), reflect two basic assumptions:

a) All heat will be retained in the conductor (adiabatic process).

b) The product of specific heat (SH) and specific weight (SW), TCAP, is approximately constant because SH increases and SW decreases at about the same rate.  For most metals, these premises are applicable over a reasonably wide temperature range, as long as the fault duration is within a few seconds.

11.3.1.1  Alternate formulations

TCAP can be calculated for materials not listed in table 11-1 from the specific heat and specific weight.  Specific heat, SH, in cal/(gram·oC) and specific weight, SW, in gram/cm3 are related to the thermal capacity per unit volume in  J/(cm3·oC) as follows:


4.184 J = 1 calorie

Therefore, TCAP is defined by;


TCAP [cal/(cm3(oC)] =  SH [cal/(gram·oC)] · SW (gram/cm3) 

or 


TCAP [J/( cm3 ·oC)] = 4.184 (J/cal) · SH [(cal/(gram·oC)] · SW (gram/cm3)
(38)

Once TCAP is determined, equations (36) and (37) can be used to determine the ampacity of the conductor.

Eequations (36) and (37) can be arranged to give the required conductor size as a function of conductor current.






(39)






(40)

Example:  A tabulation can be made, using equation (40) and table 11-1, to get data for 30 percent and 40 percent copper-clad steel, and for 100 percent and 97 percent copper conductors.  For instance, to calculate the 1 s size of a 30 percent copper-clad steel conductor, one gets:


tc = 1.0, (20 = 0.003 78, (20 = 5.86, TCAP = 3.85, Tm = 1084, Ta = 40, K0 = 245

Thus, for I = 1 kA and using equation (40):





0
11.3.1.2  Formula simplification

The formula in English units can be simplified to the following:





 
(41)

where
Akcmil
is the area of conductor in kcmil 
I
is the rms  fault current in kA 
tc
is the current duration in s

Kf
is the constant from table 11-2 for the material at various values of Tm (fusing temperature or limited conductor temperature based on 11.3.3) and using ambient temperature (Ta) of 40 oC
Table 11-2

Material constants
Material
Conductivity
(%)
Tma
(oC) 
Kf

Copper, annealed soft-drawn

100.0

1083

7.00

Copper, commercial hard-drawn

97.0

1084

7.06

Copper, commercial hard-drawn

97.0

250

11.78

Copper-clad steel core wire

40.0

1084

10.45

Copper-clad steel core wire

30.0

1084

12.06

Copper-clad steel core rod

20.0

1084

14.64

Aluminum EC Grade

61.0

657

12.12

Aluminum 5005 Alloy

53.5

652

12.41

Aluminum 6201 Alloy

52.5

654

12.47

Aluminum-clad steel core

20.3

657

19.92

Steel 1020

10.8

1510

15.95

Stainless clad steel core rod

9.8

1400

14.72

Zinc-coated steel core rod

8.6

419

28.96

Stainless steel 304

2.4

1400

30.05

aSee 11.3.3 for comments concerning material selection.
EXAMPLES:  Using the above for a 20 kA, 3 s fault;


A)
For soft drawn copper,






Akcmil
= 20 x 7.00 








= 242.5 kcmil






use 250 kcmil


B)
For 40 percent conductivity copper-clad steel conductor,






Akcmil
= 20 x 10.45 


0






= 362.0 kcmil






use 19/#7


C)
For bare steel conductor,






Akcmil
= 20 x 15.95  








= 552.5 kcmil






use 7/8  inch diameter conductor
0
One can also compare the fusing currents of a stated conductor size for various durations of time.  Using 4/0 AWG (211.6 kcmil) soft drawn copper as an example:


If tc = 0.5 sec; I = 211.6 / (7.00 


 )= 42.7 kA


If tc = 1.0 sec; I = 211.6 / (7.00 


 )= 30.2 kA


If tc = 3.0 sec; I = 211.6 / (7.00 

 
 )= 17.5 kA


The conductor size actually selected is usually larger than that based on fusing because of factors such as: 

a) The conductor should have the strength to withstand any expected mechanical and corrosive abuse during the design life of the grounding installation.

b) The conductor should have a high enough conductance to prevent any possible dangerous voltage drop during a fault, for the life of the grounding installation.

c)  The need to limit the conductor temperature. (See 11.3.3)
d) A factor of safety should be applied to the grounding system as with other electrical components.

11.3.2  Asymmetrical currents

11.3.2.1  Using decrement factor
In cases where accounting for a possible dc offset component in the fault current is desired, an equivalent value of the symmetrical current, IF, representing the effective value of an asymmetrical  current integrated over the entire fault duration, tc, can be determined as a function of X/R by using the decrement factor Df, equation (74) in 15.10, prior to the application of equations (36) through (41).





( 42)

The resulting value of IF  is always larger because the decrement factor is based on a very conservative assumption that the ac component does not decay with time but remains constant at its initial subtransient value.

11.3.2.2  Using asymmetrical current tables

Because the dc offset in the fault current will cause the conductor to reach a higher temperature for the same fault conditions (fault current duration and magnitude), equation (42) determines an equivalent value of the symmetrical current in the presence of dc offset.  In addition, if present, dc offset will result in mechanical forces and absorbed energy being almost 4 times the value than for an equivalent symmetric current case.  However, the effect of dc offsets can be neglected if the duration of the current is greater than or equal to 1 s or the X/R ratio at the fault location is less than 5.

Fusing characteristics for various sizes of copper conductor with various degree of dc offset are presented in tables 11-3 through 11-6.  These have been derived theoretically and then extensively verified experimentally [B ?? vainberg]

11.3.3  Additional conductor sizing factors

The designer should take precautions to ensure that the temperature of any conductor and connection in the grounding installation does not pose a danger to the safe operation of the substation.  For instance:

a) Typically, conductors and connections near flammable materials should be subject to more stringent temperature limitations.

b) If the strength of hard drawn copper is required for mechanical reasons, then it may be prudent not to exceed 250 oC to prevent annealing of the conductors.

The possible exposure to a corrosive environment should be carefully examined.  Even when the correct conductor size and the selected joining (connecting) method have satisfied all the IEEE Std 837 test requirements, it may be prudent to choose a larger conductor size to compensate for some gradual reduction in the conductor cross-section during the design life of the installation where  the soil environment tends to promote corrosion.

The down leads from the equipment to the grid may be subjected to the total fault current into the grid, while the grid divides this current so that each conductor segment in the grid is only subjected to some fraction of the total  fault current. Thus, the down leads may have to be larger than the grid conductors or may have to be multiples from the equipment to the grid in order to have sufficient ampacity for the total fault current.

Ground lead conductors conducting lightning current seldom require further consideration. The size of the conductor, which is selected according to its fault current requirements, usually is also adequate for carrying short time surges caused by lightning.

In practice, the requirements on mechanical reliability will set the minimum conductor size.While it might seem proper for the designer to establish minimum sizes in light of local conditions, the need for conservatism deserves consideration. Some of the specific reasons are:

a) Relay malfunctions can result in fault duration in excess of primary clearing times.  The back-up clearing time is usually adequate for sizing the conductor.  For smaller substations, this may approach 3 s or longer.  However because large substations usually have complex or redundant protection schemes, the fault will generally be cleared in 1 s or less.

b) The ultimate value of current used to determine the conductor size should take into account the possibility of future growth.  It is less costly to include an adequate margin in conductor size during the initial design than to try to reinforce a number of ground leads at a later date.

11.4  Selection of connections

All connections made in a grounding network above and below ground should be evaluated to meet the same general requirements of the conductor used; namely electrical conductivity, corrosion resistance, current carrying capacity, and mechanical strength.  These connections should be massive enough to maintain a temperature rise below that of the conductor and to withstand the effect of heating, be strong enough to withstand the mechanical forces caused by the electromagnetic forces of maximum expected fault currents and be able to resist corrosion for the intended life of the installation. 

IEEE Std 837 provides detailed information on the application and testing of permanent connections for use in substation grounding.  Grounding connections that pass IEEE Std 837 for a particular conductor size range and material should satisfy all the criteria outlined above for that same conductor size range and material.

12.  Soil characteristics
12.1  Soil as a grounding medium

The behavior of a ground electrode buried in soil can be analyzed by means of the circuit in Figure 12-1.  As shown, most soils behave both as a conductor of resistance r, and as a dielectric.  Except for high‑frequency and steep‑front waves penetrating a very resistive soil material, the charging current is negligible in comparison to the leakage current, and the earth can be represented by a pure resistance.

12.2  Effect of voltage gradient

The soil resistivity is not affected by a voltage gradient unless the latter exceeds a certain critical value.  The value somewhat varies with the soil material, but it usually has the magnitude of several kilovolts per centimeter.  Once exceeded, arcs would develop at the electrode surface and progress into the earth so as to increase the effective size of the electrode, until gradients are reduced to values that the soil material can withstand.  This condition is illustrated by the presence of gaps in Figure 12-1.  Because the substation grounding system normally is designed to comply with far more stringent criteria of step and touch voltage limits, the gradient can always be assumed to be below the critical range.

12.3  Effect of current magnitude

Soil resistivity in the vicinity of ground electrodes may be affected by current flowing from the electrodes into the surrounding soil.  The thermal characteristics and the moisture content of the soil will determine if a current of a given magnitude and duration will cause significant drying and thus increase the effective soil resistivity.  A conservative value of cur​rent density, as given by Armstrong [B3], is not to exceed 200 A/m2 for 1 s.

12.4  Effect of moisture temperature and chemical content

Electrical conduction in soils is essentially electrolytic.  For this reason the resistivity of most soils rises abruptly whenever the moisture content accounts for less than 15 percent of the soil weight.  The amount of moisture further depends upon the grain size, compactness, and variability of the grain sizes.  However, as shown in Figure 12-2, curve 2, the resistivity is little affected once the moisture content exceeds approximately 22 percent, as shown in IEEE Std 142-1991.

The effect of temperature on soil resistivity is nearly negligible for temperatures above the freezing point.  At 0 oC, the water in the soil starts to freeze and the resistivity increases rapidly.  Curve 3 shows this typical variation for a sandy loam soil containing 15.2 percent of moisture by weight.

 FIGURE 12-1 {old fig 15}

Figure 12-1
Soil model
 FIGURE 12-2 {old fig 16}
Figure 12-2

Effects of moisture, temperature, and salt upon soil resistivity
The composition and the amount of soluble salts, acids, or alkali present in the soil may considerably affect its resistivity.  Curve 1 of figure 12-2 illustrates a typical effect of salt (sodium chloride) on the resistivity of a soil containing 30 percent mois​ture by weight [B143].

Figure 12-2 should not be used for calculation purposes.  To determine the actual soil resistivity, tests such as those described in IEEE Std 81‑1983 should be performed at the site.

12.5  Use of surface material layer

Gravel or surface material coverings, usually about 0.08 to 0.15 m (3 to 6 in) in depth, are very useful in retarding the evaporation of moisture and thus in limiting the drying of topsoil layers during prolonged dry weather periods.  Also, as discussed in 7.4, covering the surface with a material of high resistivity is very valuable in reducing shock currents.  The value of this layer in reducing shock currents is not always fully realized.  Tests by Bodier at a substation in France showed that  the  river  gravel used as yard surfacing when moistened had a resistivity of 5000 ‑m resistivity with body currents while standing on dry sod.  The current in the case of dry sod was of the order of 20 times the value for wet coarse gravel.  Tests reported by Elek provide further confirmation of these benefits [B17], [B54], [B85].
‑m.  A layer 0.1 to 0.15 m (4 to 6 in) thick decreased the danger factor (ratio of body to short‑circuit current) by a ratio of 10:1, as compared to the natural moist ground.  Tests by Langer in Germany compared body currents when touching a hydrant while standing on wet coarse gravel of 6000  
In basing calculations on the use of a layer of clean surface material or gravel, consideration should be given to the possibility that insulation may become impaired in part through filling of voids by compression of the lowest ballast layers into the soil beneath by material from subsequent excavations, if not care​fully removed, and in some areas, by settlement of airborne dust.

The range of resistivity values for surface material layer depends on many factors, some of which are kinds of stone, size, condition of stone (that is, clean or with fines), amount and type of moisture content, atmospheric contamination, etc.  Table 12-1 indicates that the resistivity of the water with which the rock is wet has considerable influence on the measured resistivity of the surface material layer.  Thus, surface material subjected to sea spray may have substantially lower resistivity than surface material utilized in arid environments.  Historically, a value of 3000 ‑m has been used for the resistivity of wet surface material.  However, as indicated by table 12-1, local conditions, size, and type of stone, etc, may dictate the use of a higher or lower value of resistivity.  Thus, it is important that the resistivity of rock samples typical of the type being used in a given area be measured.

Table 12-1 gives typical resistivity values for different types of surface material measured by two different parties in different regions of the country.  These values are not valid for all types and sizes of stone in any given region.  As stated above, tests should be performed to determine the resistivity of the stone typically purchased by the utility.

Table 12-1 should not be used for calculation purposes.  To determine the actual surface material resistivity, tests should be performed.

Table 12-1

Typical surface material resistivities

???Jeff to work on paper


Resistivity of sample ((-m)



Description of rock sample
Dry
Wetted with

ground water
Wetted with

salt water

Crusher run granite (with fines) [B80]
141.8x106 
1318.7  
705.0  

#57 clean granitea[B80]
192.5x106 
8106.8  
2166.5  

Clean limestoneb[B80] 
7.3x106 to 68.5x106
2094.8 to 2912.4

1274.8 to 1470.8

Gravel (type and size unknown) [B2]
1.22x106
8534.4  
24.4 

Crushed rock (type and size unknown) [B2]
18.3x106
4267.2  
121.9 

aStandard size designation from ASTM D448-80 [???B?], approximately 0.75-1.0 in.

bNonstandard size=actual gradings as follows: 100 percent passing 1.0 in screen, 85 to 95 percent passing 0.75 in screen, 15 to 25 percent passing 0.5in screen, 5 to 10 percent passing 0.375 in screen, 0 to 2 percent passing #4 mesh.

13.  Soil structure and selection of soil model

13.1  Investigation of soil structure

Resistivity investigations of a substation site is essential for determining both the general soil composition and degree of homogeneity.  Boring test samples and other geological investigations often provide useful information on the presence of various layers and the nature of soil material, leading at least to some ideas as to the range of resistivity at the site.

13.2  Classification of soils and range of resistivity

A number of tables exist in the literature, showing the ranges of resistivity for various soils and rocks.  The tabulation from Rudenberg [B117] has the advantage of extreme simplicity.  More detailed data are available in engineering handbooks and publications [B128], [B148].  See table 13-1.

Table 13-1

Range of earth resistivity

Type of earth
Average resistivity ((-m)

Wet organic soil
10

Moist soil
102

Dry soil
103

Bedrock
104

13.3  Resistivity measurements

Estimates based on soil classification yield only a rough approximation of the resistivity.  Actual resistivity tests therefore are imperative.  These should be made at a number of places within the site.  Substation sites where the soil may possess uniform resistivity throughout the entire area and to a considerable depth are seldom found.  Typically, there are several layers, each having a different resistivity.  Often, lateral changes also occur, but in comparison to the vertical ones, these changes usually are more gradual.  Soil resistivity tests should be made to determine any important variations of resistivity with deoth.  The number of such readings taken should be greater where the variations are large, especially if some readings are so high as to suggest a possible safety problem.

If the resistivity varies appreciably with depth, it is often desirable to use an increased range of probe spacing in order to obtain an estimate of the resistivity of deeper layers.  This is possible because, as the probe spacing is increased, the test source current penetrates more and more distant areas, in both vertical and horizontal directions, regardless of how much the current path is distorted due to the varying soil conditions [B92].

A number of measuring techniques are described in detail in IEEE Std 81-1983.  The Wenner’s four-pin method as shown in figure 13-1 is the most commonly used technique.  In brief, four probes are driven  into the earth along a straight line, at equal distances a apart, driven to a depth b.  The voltage between the two inner (potential) electrodes is then measured and divided by the current between the two outer (current) electrodes to give a value of mutual resistance R.  Then,





(42)

Where

(a 
is the apparent resistivity of the soil in (-m

R
is the resistance in ohms resulting from dividing the voltage between the potential probes by the current flow between the current electrodes

a
is the distance between adjacent electrodes in m

b
is the depth of the electrodes in m

If b is small compared to a, as is the case of probes penetrating the ground a only short distance, the above equation can be reduced to





(43)

The current tends to flow near the surface for the small probe spacing, whereas more of the current penetrates deeper soils for large spacing.  Thus, it is customary to assume that the resistivity measured for a given probe spacing a represents the apparent resistivity of the soil to a depth of a when soil layer resistivity contrasts are not excessive.  Equations (42) and (43), thus, can be used to determine the apparent resistivity (a  at a depth a.

Figure 13-1 Wenner’s four-pin method

Schlumburger-Palmer is a modified version of the above method.  This method gives greater sensitivity for large probe spacing, as described in IEEE Std 81-1983, [B111].

Another method of measuring soil resistivity, as shown in figure 13-2, is the driven-rod method based on the three-pin or fall-of-potential method. [B113], [B15], [B16]  In this method, the depth L of the driven-rod located in the soil to be tested is varied.  The other two rods, known as reference rods, are driven to a shallow depth b in a straight line.  The voltage rod is located at a distance of 62 percent of the distance from the test rod to the current rod.  For a uniform soil, the apparent resistivity is given by:





(44)

where

(a 
is the apparent resistivity of the soil in (-m

R
is the measured resistance in (
L
is the the length of the rod in m

d
is the the diameter of the rod in m

A plot of the measured apparent resistivity value (a  versus the rod length L provides a visual aid for determining earth resistivity variations with depth.

Figure 13-2 Three-pin or driven-ground rod method

Tests conducted by Ohio State University [B60] demonstrated that either the Wenner four-pin method or the driven-rod three-pin method can provide the information needed to develop a soil model.

The Wenner four-pin method is the most popular method in use.  There are a number of reason for this popularity.  The four-pin method obtains the soil resistivity data for deeper layers without driving the test pins to those layers.  No heavy equipment is needed to perform the four-pin test

An advantage of the driven-rod method, although not related necessarily to the measurements, is the ability to determine to what depth the ground rods can be driven.  Knowing if and how deep rods can be driven into the earth can save the need to redesign the ground grid. Often, because of hard layers in the soil such as rock, hard clay, etc., it becomes practically impossible to drive the test rod any further resulting in insufficient data.  A technique for the prediction of the soil resistivity to a depth 10 times the depth of known resistivity value has been developed by Blattner [B15].  This technique can be effectively used in cases where the test rod cannot be driven deep.  However, the user is advised to review practical limitations of this technique before using it.  When the test rod is driven deep in the ground, it usually looses contact with the soil due to the vibration and the larger diameter couplers resulting in higher measured resistance values.  A ground grid designed with these higher soil resistivity values may be unnecessarily conservative.  The driven-rod method presents an uncertainty in the resistance value which is measured at a 62 percent spacing.  The 62 percent rule is valid only for large electrode separation and uniform soil.  In non-uniform soils, this assumption may affect the outcome of the readings [B?? from Dawalibi]

Resistivity measurement records should include temperature data and information on the moisture content of the soil at the time of measurement.  All data available on known buried conductive objects in the area studied should also be recorded.

Buried conductive objects in contact with the soil can invalidate readings made by the methods described if they are close enough to alter the test current flow pattern.  This is particularly true for large or long objects.  For this reason, the soil resistivity measurements are likely to be significantly distorted in an area where grid conductors have already been installed, except for shallow-depth measurements in or near the center of a very large mesh rectangle.  In such cases, a few approximate readings might be taken in a short distance outside the grid, with the probes so placed as to minimize the effect of the grid on the current flow pattern.  Though not conclusive as to conditions inside the grid, such readings may be used for approximation, especially if there is reason to believe that the soil in the entire area is reasonably homogeneous.

13.4  Interpretation of soil resistivity measurements

Interpretation of apparent resistivity obtained in the field is perhaps the most difficult part of the measurement program.  The basic objective is to derive a soil model that is a good approximation of the actual soil.  Soil resistivity varies laterally and with respect with depth, depending on the soil stratification.  Seasonal variations may occur in soil resistivity due to varying weather conditions as described in [B62].  It must be recognized that the soil model is only an approximation of the actual soil conditions and that a perfect match is unlikely.

The most commonly used soil resistivity models are the uniform soil model and the two-layer soil model.  Two-layer soil models are often a good approximation of many soil structures while multi-layer soil models may be used for more complex soil conditions.  Interpretation of the soil resistivity measurements may be accomplished either manually or by use of computer analysis techniques described in numerous references. [B59], [B60], [B61], [B105], [B99], [B14], [B95], [B57], [B135], [B96], [B15], [B86], [B114], [B16]

A uniform soil model yields a single soil resistivity value only when there is a small variation in apparent resistivity.  In homogeneous soil conditions, which rarely occurs in practice, the uniform soil model may be reasonably accurate.  If there is a large variation in measured apparent resistivity, the uniform soil model is unlikely to yield accurate results.

A more accurate representation of the actual soil conditions can be obtained by use of a two-layer model.  The two-layer model consists of an upper layer of finite depth and with different resistivity than a lower layer of infinite thickness.  There are several techniques to determine an equivalent two-layer model from apparent resistivity obtained from field tests.  In some instances a two-layer model can be approximated by visual inspection of a plot of the apparent resistivity versus depth from driven rod measurements or apparent resistivity versus probe spacing from Wenner four-pin measurements. [B13], [B16], [B77]

Computer programs available to the industry may also be used to derive a two-layer soil model and multi-layer soil models. [B59], [B61], [15], [22]

In some instances the variation in soil resistivity may exhibit minimums and maximums such that an equivalent two-layer model may not yield an accurate model.  In such instances a different soil model, such as a multi-layer model, may be required as described in references [B47] [B48].

13.4.1  Uniform soil assumption

Sometimes, in a multi-layer soil, the variation in apparent soil resistivity (a with respect to depth significant. As an approximation, the soil can be considered uniform if the difference between two extreme values of apparent resistivity is less than 30 percent of the maximum value.  Such a soil may be approximated as a uniform soil with a single soil resistivity value obtained by taking an average value from measured apparent soil resistivity data as shown in equation (45).





(45)

where

(a(1), (a(2), (a(3) ...(a(n) are the apparent resistivity measurements obtained at different spacing in four-pin method or at different depths in driven ground rod method in (-m

n
is total number of measurements

A majority of the soils will not meet the above criteria.  It is difficult to develop a uniform soil model when the soil is heterogeneous.  Because equations in this guide require a uniform soil model, an attempt was made to develop a guideline to determine a uniform soil model for a wide range of non-uniform soils.  A limited number of soil data obtained from several sites using the Wenner method were interpreted by two different soil models.  Each soil was interpreted by the two-layer soil model determined from a computer program.  A uniform soil model for each soil was based on the average of the measured maximum and minimum apparent resistivity values as described in equation (46).

The grounding parameters, including grid resistance and step and touch voltages, for a 76.2x76.2 m (250x250 ft) grid with 8 meshes in each direction and with uniformly distributed ground rods were computed using a computer program.  A comparison was made between the grounding parameters computed for the two-layer model and those computed with the uniform soil model. The comparison between the grounding parameters based on these limited cases indicate a good relationship between the two-layer and the uniform soil model determined by equation (46). The investigation further indicated that, for a majority of the soils, the uniform soil model produced conservative results.  If uniform soil resistivity determined using equation (46) is employed to design a ground grid, the depth of ground rods should penetrate the depth equal to the Wenner four-pin spacing corresponding to the value of pa(av2).





(46)

where

(a (max)
is the maximum apparent resistivity value (from measured data), (-m.

(a (min)
is the minimum apparent resistivity value (from measured data), (-m.

Annex E shows details of this investigation, including the comparison of grounding parameters for two typical soils.

There are other methods suggested by authors which include determining a two layer model and using the upper layer resistivity for touch and step calculations and the lower resistivity for resistance and methods that modify the equations presented in the Guide to be used in two layer soil models.  These papers may provide the designer with more information about the interpretation of soils and the impact of multi-layer, two-layer and uniform models. [?? Dawalibi & Southey, Thapar, Farid & Nelson]

13.4.2  Nonuniform soil assumptions

Another approach to situations where resistivity varies markedly with depth is suggested by Sunde, and in some of the books on geophysical prospecting to which he refers.  For example, it is often possible from field readings taken with a wide range of probe spacing to deduce a stratification of the earth into two or more layers of appropriate thickness that will account for the actual test variations. [B99], [B128]

13.4.2.1  Two layer soil model (general)

The two layer soil is generally described by upper layer soil resistivity ((1), depth of the upper layer (h), and lower layer soil resistivity ((2).  A constant called the reflection factor is further used to quantitatively define a two layer model, as defined by equation (47).





(47)

A grounding system in a two-layer soil environment behaves differently in comparison with the same system in uniform soil.  Generally, for a grounding system in uniform soil or in two-layer soil with (1  less than (2   (upper layer soil resistivity less than lower layer soil resistivity, a positive reflection factor), the current density is higher in the conductors at the outer edges of the grounding grid.  In two-layer soil with (1  greater than (2  (the soil in the upper layer is more resistive than the lower layer soil, a negative reflection factor), the current density is more uniform over all the conductors of the grounding system.  This is caused by the tendency of the grid current to go downward into the layer of lower resistivity, rather than up and outward to the more resistive upper layer.  Studies by Thapar and Gross [B138] and Dawalibi et al. [B44] provide a wealth of information on this subject.

The equations that govern the performance of a grounding system buried in multilayer soil can be obtained by solving Laplace’s equations for a point current source, or by the method of images, which gives identical results.  The use of either method in determining the earth potential caused by a point current source results in an infinite series of terms representing the contributions of each consequent image of the point current source.  Exact formulation of the equations that include these effects is given in numerous references, for instance, [B42], [B74], and [B128].

While the most accurate representation of a grounding system should certainly be based on the actual variations of soil resistivity present at the substation site, it will rarely be economically justifiable or technically feasible to model all these variations.  However, in most cases, the representation of a ground electrode based on an equivalent two-layer earth model is sufficient for designing a safe grounding system.

IEEE Std 81-1983 provides methods for determining the equivalent resistivities of the upper and lower layer of soil and the height of the upper layer for such a model.

13.4.2.2  Two layer soil model by graphical method

A two-layer soil model can be approximated by using graphical methods described in references [B136] [B14] [B57] [B135] [B114] [B128].  The Sunde’s [B128] graphical method is described in following paragraphs.

In Sunde’s method, the graph shown in figure 13-3, is used to approximate a two-layer soil model.  The graph in figure 13-3, which is based on Wenner’s four-pin test date, is reproduced from figure-2.6 of reference [B128] with notations revised to match the symbols used in this guide.

Parameters (1, (2 and h are obtained by trial and error method as follows:

a) Plot a graph of apparent resistivity (a on y-axis vs. rod spacing a on x-axis.

b) a corresponding to a smaller spacing is (1 and that for larger spacing is (2.  Extend the apparent resistivity graph at both ends to obtain these extreme resistivity values if the field data are insufficient.  Determine (2/(1 and select corresponding graph in figure 13.3.

c) Assume an initial value of h say h, based on the slope of the graph plotted in 1.  If the slope is steep, choose a small h and vice-versa.

d) Determine ratios a/h1 corresponding to all the field data.

e) Obtain (a/(1 for each a/h1 along the curve selected in 2.

f) Divide each (a obtained in field by corresponding (a/(1, obtained in 5.  This division should produce a constant value of (1.
g) If constant value of (1 is not obtained in 6, increase or decrease h assumed in 3 and repeat steps 3 through 7.

Figure 13-3 Sunde’s graphical method

After practicing this method for a few cases, quick and accurate results can be expected.  Note that the (1 and (are visually inspected and only the depth h of the upper layer is determined accurately using the Sunde’s method.

13.4.2.3  Comparison of uniform and two-layer soil model

The two-layer model approach has been found to be much more accurate than the uniform soil model.  Some of the reasons are:

a) Variations in soil resistivity have considerable influence on the performance of most grounding systems, affecting both the value of ground resistance and ground potential rise, and the step and touch surface voltages.  In general, for negative values of K (upper layer more resistive than lower layer), the resistance is less than that of the same grounding system in uniform soil with resistivity (1.  In contrast, for positive values of K, the resistance is generally higher than that in uniform soil and resistivity (1.  A similar relationship exists for the step and touch voltages produced on the surface of a two-layer earth versus that on the surface of uniform soil.  For negative values of K, the step and touch voltages are generally lower than the voltages for the same grounding system in uniform soil of resistivity (1.  Also, for positive values of K, the step and touch voltages are generally higher than in uniform soil.

b) Other parameters, such as the surface layer height h, also affect the differences in the performance of ground electrodes in a two-layer environment and in uniform soil conditions.  The general rule is that when the upper layer height h becomes significantly larger than the electrode’s own dimensions, the performance of the electrode approaches the performance of the same electrode in uniform soil of resistivity (1.

c) Also, it must be recognized that the above characteristics are based on the premise of a constant fault current source.  The actual currents in the grounding system will change from case to case as a function of (1 and (2, reflecting the local changes relative to all other ground fault current paths predetermined by the fault location.  This current division is discussed in clause 15.  Therefore, in certain cases some of the assumptions given above may not always hold true.

For design applications involving relatively simple grounding arrangements of electrodes buried in a reasonably uniform soil, the approximate methods provided elsewhere in the guide will be suitable for obtaining a realistic design with adequate safety margins.  However, for designs involving a large grounded area, odd-shaped grids, etc., or where the resistivity of soil is clearly very nonuniform, the engineer responsible for the design should decide if more sophisticated methods are needed.

13.4.2.4  Multi-layer soil model

Highly non-uniform soil conditions may be encountered.  Such soil conditions may require the use of multilayer modeling techniques if an equivalent two-layer soil model is not feasible.  A multilayer soil model may include several horizontal layers or vertical layers.  Techniques to interpret highly non-uniform soil resistivity require the use of computer programs [B59], [B61], [B47], [B48] or graphical methods [B109].

14.  Evaluation of ground resistance
14.1  Usual requirements

A good grounding system provides a low resistance to remote earth in order to minimize the GPR.  For most transmission and other large substations, the ground resistance is usually about 1 , depending on the local conditions.
 or less.  In smaller distribution substations the usually acceptable range is from 1 to 5 
14.2  Simplified calculations

Estimation of the total resistance to remote earth is one of the first steps in determining the size and basic layout of a grounding system.  The resistance depends primarily on the area to be occupied by the grounding system, which is usually known in the early design stage.  As a first approximation, a minimum value of the substation grounding system resistance in uniform soil can be estimated by means of the formula of a circular metal plate at zero depth:





(48)

where

Rg
is the substation ground resistance in 
(
is the average earth resistivity in ‑m

A
is the area occupied by the ground grid in m2
Next, an upper limit of the substation ground resistance can be obtained by adding a second term to the above formula, as proposed by Laurent [B87] and Niemann [B106]:





(49)

where 

LT 
is the total buried length of conductors in m

In the case of a grid rod combination in uniform soil, a combined length of horizontal conductors and ground rods will yield a slightly conservative estimate of LT , because ground rods usually are more effective on a per unit length basis.

The second term recognizes the fact that the resistance of any actual grounding system that consists of a number of conductors is higher than that of a solid metallic plate, and that the difference will decrease with the increasing length of buried conductors, approaching 0 for infinite LT , when the condition of a solid plate is reached.

Sverek expanded equation (49) to take into account the effect of non-zero grid depth. [B131]





(50)

where


h
is the depth of the grid in m

For grids without ground rods, this formula has been tested to yield results that are practically identical to those obtained with equation (52) of Schwarz, described in 14.3.

The following tabulation from Kinyon [B82] offers some idea of how the calculated and actual measured resistance for five different substations compare. equation (49) was used to compute the grid resistance.  See table 14-1.

Table 14-1

*Typical grid resistances
Table 14-1 {old table 5} 

* An average value of all measured resistivity values is frequently substituted for the uniform soil resistivity in equation (49).  If this average resistivity is used, equation (49) usually produces a resistance that is higher than the value that would result from a direct resistance measurement.  The calculated and measured resistance values shown above do not reflect this trend, because Kinyon based his calculations on the "... lowest average value of resistivity measured on the site."  Readers are referred to Kinyon for further discussion on his choice of resistivity values used in table 14-1. [B82]

14.3
Schwarz's equations

Schwarz developed the following set of equations to determine the total resistance of a grounding system in a homogeneous soil consisting of horizontal (grid) and vertical (rods) electrodes. [B122]  Schwarz’s equations extended accepted equations for a straight horizontal wire to represent the ground resistance, R1 , of a grid consisting of crisscrossing conductors, and a sphere embedded in the earth to represent ground rods, R2.  He also introduced an equation for the mutual ground resistance Rm between the grid and rodbed.  Schwarz used the following equation introduced by Sunde [B128] and Rudenberg [B118] to combine the resistance of the grid, rods and mutual ground resistance to calculate the total system resistance, Rg.





(51)

where:

R1
ground esistance of grid conductors

R2
ground resistance of all ground rods

Rm
mutual ground resistance between the group of grid conductors, R1,  and group of ground rods, R2
Ground resistance of the grid:





(52)

where

-m

is the soil resistivity, 
Lc
is the total length of all connected grid conductors in m

a

is for conductors buried at depth h, in m

or

a’
is a for conductor on earth surface

2a
is the diameter of conductor in m

A
is the area covered by conductors in m2
k1, k2
are the coefficient [see figures 14-1(a) and 14-1(b)]

Ground resistance of the rodbed:





(53)

where

Lr
is the length of each rod, m

2b
is the diameter of rod, m

nR
number of rods placed in area A

Mutual ground resistance between the grid and the rod bed:





(54)
The combined ground resistance of the grid and the rod bed will be lower than the ground resistance of either component alone, but still higher than that of a parallel combination.

Schwarz compared the results of his equations to previously published theoretical work and to model tests to verify the accuracy of his equations.  Since their publication in 1954, Schwarz’s equations have been modified by Kercel [B81] to provide equations for constants k1 and k2 and further expanded to include the use of equations in two-layer soil. [B103] [B104]

14.4  Note on ground resistance of primary electrodes

In general, the ground resistance of any primary electrode depends on the soil resistivity and the size and type of arrangement of all individual conductors comprising the ground electrode.  In more complex arrangements involving crisscrossed wires and a large number of rods in the same area, the mutual resistance between individual elements plays an important role. More literature exists on this aspect of accurate evaluation of grounding systems than any other.  For studies utilizing computers, numerous references are available.

14.5  Soil treatment to lower the resistivity

It is often impossible to achieve the desired reduction in ground resistance by adding more grid conductors or ground rods.  An alternate solution is to effectively increase the diameter of the electrode by modifying the soil surrounding the electrode.  The inner shell of soil closest to the electrode normally comprises the bulk of the electrode ground resistance to remote earth.  This phenomenon is often utilized to an advantage, as follows:

a) Use of sodium chloride, magnesium, and copper sulfates, or calcium chloride, to increase the conductivity of the soil immediately surrounding an electrode.  State or Federal authorities may not permit using this method because of possible leaching to surrounding areas.  Further, the salt treatment must be renewed periodically. 

b) Use of bentonite, a natural clay containing the mineral montmorillionite, which was formed by volcanic action years ago.  It is noncorrosive, stable, and has a resistivity of 2.5 ‑m, at 300 percent moisture.  The low resistivity results mainly from an electrolytic process between water, Na2O (soda), K2O(potash), CaO (lime), MgO (magnesia), and other mineral salts that ionize forming a strong electrolyte with pH ranging from 8 to 10.  This electrolyte will not gradually leach out, as it is part of the clay itself.  Provided with a sufficient amount of water, it swells up to 13 times its dry volume and will adhere to nearly any surface  it touches.  Due to its hygroscopic nature, it acts as a drying agent drawing any available moisture from the surrounding environment.  Bentonite needs water to obtain and maintain its beneficial characteristics.  Its initial moisture content is obtained at installation when the slurry is prepared.  Once installed, bentonite relies on the presence of ground moisture to maintain its characteristics.  Most soils have sufficient ground moisture so that drying out is not a concern.  The hygroscopic nature of bentonite will take advantage of the available water to maintain its as installed condition.  If exposed to direct sunlight, it tends to seal itself off, preventing the drying process from penetrating deeper.  It may not function well in a very dry environment, because it may shrink away from the electrode, increasing the electrode resistance. [B79]

c) Chemical type electrodes consist of a copper tube filled with a salt.  Holes in the tube allow moisture to enter, dissolve the salts and allow the salt solution to leach into the ground.  These electrodes are installed in an augured hole and typically back‑filled with soil treatment.

d) Ground enhancement materials, some with a resistivity of less than 0.12 -m (about 5 percent of the resistivity of bentonite), are typically placed around the rod in an augured hole or around grounding conductors in a trench, in either a dry form or premixed in a slurry.  Some of these enhancement materials are permanent and will not leach any chemicals into the ground.  Other available ground enhancement materials are mixed with local soil in varying amounts and will slowly leach into the surrounding soil, lowering the earth resistivity.

FIGURE 14-1 (a)
{Old Fig 18}

Figure 14-1
Coefficients k1, and k2 of Schwarz's formula
(a)  Coefficient k1
FIGURE 14-1 (b)
{Old Fig 18}

Figure 14-1 (Continued)
(b) Coefficient k2
14.6  Concrete-encased electrodes

Concrete, being hygroscopic, attracts moisture.  Buried in soil, a concrete block behaves as a semiconducting medium with a resistivity of 30 to 90 ‑m.  This is of particular interest in medium and highly resistive soils because a wire or metallic rod encased in concrete has lower resistance than a similar electrode buried directly in the earth.  This encasement reduces the resistivity of the most critical portion of material surrounding the metal element in much the same manner as does a chemical treatment of soils.  However, this phenomenon may often be both a design advantage and disadvantage.  Some of the reasons are:

a) On the one hand, it is impractical to build foundations for structures where the inner steel (reinforcing bars) is not electrically connected to the metal of the structure.  Even if extreme care were taken with the anchor bolt placement in order to prevent any direct metal‑to‑metal contact, the semiconductive nature of concrete would provide an electrical connection.

b) On the other hand, the presence of a small dc current can cause corrosion of rebar material.  Although ac current as such does not produce corrosion, approximately 0.01 percent of the ac current becomes rectified at the interface of the steel bar and concrete [B115].

c) Splitting of concrete may occur either due to the above phenomenon because corroded steel occupies approximately 2.2 times its original volume, producing pressures approaching 35 MPa.  The passage of a very high current, which would vaporize the moisture in the concrete.

Fortunately, there is a certain threshold potential for dc corrosion, approximately 60 V dc, below which no corrosion will occur.  A number of field tests concerning the maximum current loading is reported in the literature. [B19], [B52], [B97]  The short‑time current loading capacity, ICE, of concrete‑encased electrodes can be estimated by means of Ollendorf's formula
 for an indefinitely sustainable current I, adjusted by a 1.4 multiplying factor, or directly from figure 14-2.





(55)

where

g
is the thermal conductivity of the earth in W/(m °C)

Rz
is the ground resistance of the concrete‑encased electrode in 
‑m

is the soil resistivity in 
Ta
is the ambient temperature in °C

Tv
is the maximum allowable temperature to prevent sudden evaporation of moisture in °C

I
is the indefinitely sustainable current in A

FIGURE 14-2 {old fig 19}
Figure 14-2
Short-time current loading capability of concrete-encased ground electrodes
The applicability of this formula has been verified in [B19], which reports on the results of extensive field testing of concrete poles.  In general, if damage is to be prevented, the actual current should be less than the value of ICE determined by equation (55).  A 20 to 25 percent safety margin is reasonable for most practical applications.  

Thus, with proper precautions, the concrete‑encased foundations may be used as auxiliary ground electrodes.

Bibliographic reference [B64] uses the following equation for obtaining the ground resistance, RCE-rod , of a vertical rod encased in concrete:





(56)

where

‑m
c
is the resistivity of the concrete in 
‑m

is the resistivity of the soil in 
Lr
is the length of the ground rod in m

d
is the diameter of the ground rod in m

D
is the diameter of the concrete shell in m

The above equation can be related to the commonly used formula for a ground rod of length Lr and diameter d, as shown below,





(57)

then Equation (56) can be resolved into





(58)

representing a combination of two resistances in series:

a) Ground resistance calculated by equation (57) of a concrete cylinder of diameter D, directly buried in soil 
b) Ground resistance of the inner segment of diameter D, containing a metal rod of diameter d
Obviously, the latter term is obtained as a difference of the hypothetical resistance values for a rod in concrete, if d and D are entered into the single‑medium formula equation (57), and c.
 is replaced by 
Such an approach is generally valid for any other electrode having a different shape.  Noting, for convenience,


RSM  = F((,So,G)
(59)


RDM  = F((c, So , G) + F((, Si , G) - F((c, Si , G)
(60)

where, in addition to the symbols already mentioned,

RSM
is the electrode resistance in single medium in (
RDM
is the electrode resistance in dual medium in (
S0
is the surface area of a given electrode in m2
Si
is the area of interface in m2
G
is a certain geometrical factor characterizing the particular shape of a given electrode

This form is adaptable to a variety of electrodes, buried in soil, and assumed to be surrounded by a concentric shell of a material that has different resistivity than the soil.  One possible model of this type, for which Schwarz's formula for a rodbed can easily be modified, is shown in figure 14-3.

FIGURE 14-3 {old fig 20}

Figure  14-3
Grid with encased vertical electrodes
Recommendations:

a)
Connect anchor bolt and angle stubs to the reinforcing steel for a reliable metal‑to‑metal contact.

b)
Reduce the current duty and dc leakage to allowable levels by making sure that enough primary ground electrodes (grounding grid and ground rods) will conduct most of the fault current.

c)
Soil enhancement material may be used in the areas of a high soil resistivity to reduce the resistance of primary grounding.  Augering a 150 to 250 mm (6 to 10 in) hole and backfilling it with a soil enhancement material around a ground rod is a useful method to prevent the predominance of auxiliary electrodes in dissipating the fault current.

15.  Determination of maximum grid current

15.1  Definitions

15.1.1  dc offset: Difference between the symmetrical current wave and the actual current wave during a power system transient condition.  Mathematically, the actual fault current can be broken into two parts, a symmetrical alternating component and a unidirectional (dc) component, with decreasing magnitudes.  The unidirectional component can be of either polarity, but will not change polarity, and will decrease at some predetermined rate.

15.1.2  dc offset factor: Ratio of the peak fault current to the peak symmetrical value.

15.1.3  fault current division factor: A factor representing the inverse of a ratio of the symmetrical fault current to that portion of this current that flows between the grounding grid and surrounding earth.

NOTE: In reality, the current division factor would change during the fault duration, based on the varying decay rates of the fault contributions and the sequence of interrupting device operations.  However, for the purposes of calculating the design value of maximum grid current and symmetrical grid current per definitions of symmetrical grid current and maximum grid current, the ratio is assumed constant during the entire duration of a given fault.  Consequently, this factor may be expressed as





(61)

where

Ig
is the symmetrical grid current in A

I0
is the zero‑sequence fault current in A

15.1.4  maximum grid current: A design value of the maximum grid current,  defined as follows:





(62)

where

IG
is the maximum grid current in A

Df
is the decrement factor for the entire duration of fault tf, found for tf given in s

Ig
is the rms symmetrical grid current in A

15.1.5  subtransient reactance: Reactance of a generator at the initiation of a fault.  This reactance is used in calculations of the initial symmetrical fault current.  The current continuously decreases, but it is assumed to be steady at this value as a first step, lasting approximately 0.05 s after a suddenly applied fault.

15.1.6  symmetrical grid current: That portion of the symmetrical ground  fault current that flows between the grounding grid and surrounding earth.   It may be expressed as:





(63)

where

Ig
is the symmetrical grid current in A

If 
is the rms value of symmetrical ground fault current in A

Sf
is the current division factor relating the magnitude of fault current to that portion of this current flowing between the grounding grid and surrounding earth

15.1.7  synchronous reactance: Steady‑state reactance of a generator during fault conditions used to calculate the steady‑state fault current.  The current so calculated excludes the effect of the automatic voltage regulator or governor.

15.1.8  transient reactance: Reactance of a generator between the subtransient and synchronous states.  This reactance is used for the calculation of the symmetrical fault current during the period between the subtransient and steady states.  The current decreases continuously during this period, but is assumed to be steady at this value for approximately 0.25 s.

15.1.9  X/R ratio: Ratio of the system inductive reactance to resistance.  It is proportional to the time constant L/R, and is, therefore, indicative of the rate of decay of any dc offset.  A large X/R ratio corresponds to a large time constant and a slow rate of decay.

15.2  Procedure

In most cases, the largest value of grid current will result in the most hazardous condition.  For these cases, the following steps are involved in determining the correct design value of maximum grid current IG for use in substation grounding calculations:

Step (a)  Assess the type and location of those ground faults  that are likely to produce the greatest flow of current between the grounding grid and surrounding earth, and hence the greatest rise in grid potential with respect to remote earth (GPR) and largest local surface potential gradients in the substation area.

Step (b)  Determine, by computation, the fault current division factor Sf  for the faults selected in Step (a), and establish the  corresponding values of symmetrical grid current Ig.

Step (c)  For each fault, based on its duration time tf, determine the value of decrement factor Df to allow for the effects  of asymmetry of the fault current wave.

Step (d)  Select the largest product Df Ig, and hence the worst  fault condition.

15.3  Types of ground faults

Many different types of faults may occur in the system.  Unfortunately, it may be difficult to determine which fault type and location will result in the greatest flow of current between the ground grid and surrounding earth because no simple rule applies.  Figures 15-1, 15-2, 15-3, and 15-4 show maximum grid current IG for various fault locations and system configurations.

In determining the applicable fault types, consideration should be given to the probability of occurrence of the fault.  Multiple simultaneous faults, even though they may result in higher ground current, need not be considered if their probability of occurrence is negligible.  It is thus recommended, for practical reasons, that investigation be confined to single‑line‑to‑ground and line‑to‑line‑to‑ground faults. 

Figure 15-1 {old fig 21}

Figure 15-1

Fault within local substation; local neutral grounded

Figure 15-2 {old fig 22}
Figure 15-2

Fault within local substation; neutral grounded at remote location

Figure 15-3 {old fig 23}
Figure 15-3

Fault in substation: system grounded at local substation and also at other points

Figure 15-4 {old fig 24}

Figure 15-4

Typical current division for a fault on high side of distribution substation

In the case of a line‑to‑line‑to‑ground fault, the zero sequence fault current is:





(64)

where

I0
is the symmetrical rms value of zero sequence fault current in A

E
is the phase‑to‑neutral voltage in V

Rf
is the estimated resistance of the fault,  (normally it is assumed Rf = 0)

R1
is the positive sequence equivalent system resistance, /phase

R2
is the negative sequence equivalent system resistance, /phase

R0
is the zero sequence equivalent system resistance, /phase

X1
is the positive sequence equivalent system reactance (subtransient), /phase

X2
is the negative sequence
 equivalent system reactance, /phase

X0
is the zero sequence equivalent system reactance, /phase

The values R1, R2, R0, X1, X2, and X0 are computed looking into the system from the point of fault.

In the case of a single‑line‑to‑ground fault, the zero sequence fault current is:





(65)

In many cases, however, the effect of the resistance terms in the above equation is negligible.  For practical purposes, the following simplified equations are sufficiently accurate and more convenient:

Zero sequence current for line-to-line-to-ground fault:





(66)

Zero sequence current for line-to-ground fault:





(67)

15.4  Effect of substation ground resistance

In most cases it is sufficient to derive the maximum grid current IG, as described in 15.2 and 15.3, by neglecting the system resistance, the substation ground resistance, and the resistance at the fault.  The error thus introduced is usually small, and is always on the side of safety.  However, there may be unusual cases where the predicted substation ground resistance is so large, in relation to system reactance, that it is worthwhile to take the resistance into account by including it into the more exact equation (64) or (65).  This poses a problem because the substation ground system is not yet designed and its resistance is not known. However, the resistance can be estimated by the use of the approximate formulas of 14.2 or 14.3. This estimated resistance generally gives sufficient accuracy for determining the current Ig, and hence IG.

15.5  Effect of fault resistance

If the fault is an insulation breakdown within the local substation, the only safe assumption is that the resistance of the fault be assumed zero (figures 15-1, 15-2, 15-3, and 15-4).

In the case of a fault outside of the local substation area, on a line connected to the substation bus (figure 15-4), it is permissible, if a conservative (minimum) value of fault resistance Rf can be assigned, to use this in the ground fault current calculations.  This is done by multiplying Rf  by 3 and adding it to the other resistance terms as indicated in the denominator of equations (64) through (67).  If, however, the actual fault resistance does not maintain a value at least as great as the value of Rf  used in the calculations, then the fault resistance should be neglected.  Any error from neglecting Rf  will, of course, be on the side of safety.

15.6  Effect of overhead ground wires and neutral conductors

Where transmission line overhead ground wires or neutral conductors  are connected to the substation ground, a substantial portion of the ground fault current is diverted away from the substation ground grid. Where this situation exists, the overhead ground wires or neutral conductors should be taken into consideration in the design of the ground grid.

Connecting the substation ground to overhead ground wires or neutral conductors, or both, and through them to transmission line structures or distribution poles, will usually have the overall effect of increasing the GPR at tower bases, while lessening it at the substation.  This is due to the fact that each of the  nearby towers will share in each voltage rise of the substation ground mat, whatever the cause, instead of being affected only by a local insulation failure or flashover at one of the towers.  Conversely, when such a tower fault does occur, the effect of the connected substation ground system should decrease the magnitude of gradients near the tower bases.

15.7  Effect of direct buried pipes and cables

Buried cables with their sheaths or armor in effective contact with the ground, and buried metallic pipes will have a somewhat similar effect when they are bonded to the substation ground system, but extend beyond its perimeter.

Buried cables with their sheaths or armor in effective contact with the earth, and buried metallic pipes bonded to the substation ground system and extending beyond its perimeter will have an effect similar to that of overhead ground wires and neutrals.  By conducting part of the ground fault current away from the substation, the potential rise of the grid during the fault, and the local gradients in the substation will be somewhat lessened.  As discussed in clause 15, external hazards may sometimes be introduced. [B18], [B117]

Because of the complexities and uncertainties in the pattern of current flow, the effect is often difficult to calculate.  Some guidelines to the computation of the input impedance of such current paths leaving the substation are supplied by Rudenberg [B76] and Laurent [B53].  A more recent study of this problem is presented in [B102], which provides methods for computing the impedance of both above‑ground and buried pipes.  From these values an approximate calculation can determine the division of ground current between these paths, the substation ground system, and any overhead ground wires that are present and connected.

15.8  Worst fault type and location - step (a)

The worst fault type for a given grounding system is usually the one resulting in the highest value of the maximum grid current IG.  Because this current is proportional to the zero sequence or ground fault current and the current division factor, and because the current division is almost independent of the fault type, the worst fault type can be defined as the one resulting in the highest zero sequence or ground fault current flow into the earth, 3I0.  In a given location, a single-line‑to‑ground fault will be the worst fault type if Z0Z1 > Z22 at the point of fault, and a line‑to‑line‑to‑ground fault will be the worst type if Z1Z0 < Z22.  In the usual case where Z2 is assumed equal to Z1, the above comparisons reduce to Z0 > Z1, and Z0 < Z2, respectively.

The question of the fault location producing the maximum grid current IG involves several considerations.  The worst fault location may be either on the high voltage side or on the low voltage side, and in either case may be either inside the substation or outside on a line, at a certain distance from the substation.  A fault is classified as inside the substation if it is related to a metallic structure that is electrically connected to the substation grounding grid via negligible impedance.  There are no universal rules for the determination of the worst fault location.  The following discussion relates to some, but by no means all, possibilities.

For distribution substations with the transformer grounded only on the distribution side, the maximum grid current IG usually occurs for a ground fault on the high side terminals of the transformer.  However, if the source of ground fault current on the high side is weak, or if a parallel operation of several transformers results in a strong ground fault current source on the low side, the maximum grid current may occur for a ground fault somewhere on the distribution circuit.

For ground faults on the low side terminals of such a secondary grounded transformer, the transformer's contribution to the fault circulates in the substation grid conductor with negligible leakage current into the earth and, thus, has no effect in the sub​station ground potential rise (GPR), as shown in figure 15-1.

For ground faults outside the substation on a distribution feeder (far enough to be at remote earth with respect to the ground grid), a large portion of the fault current will return to its source (that is, the transformer neutral) via the substation grid, thus contributing to the substation GPR.

In transmission substations with three‑winding transformers or autotransformers, the problem is more complex.  The maximum  grid current IG may occur for a ground fault on either the high or low side of the transformer; both locations should be checked.  In either case, it can be assumed that the worst fault location is at the terminals of the transformer inside the substation, if the system contribution to the fault current is larger than that of the transformers in the substation.  Conversely, the worst fault location may be outside the substation on a transmission line, if the transformer contribution dominates.  

Exceptions to the above generalities exist.  Therefore, for a specific system, several fault location candidates for the maximum grid current should be considered.  For each candidate, the applicable value of zero sequence current I0 (ground fault current) should be established in this step.

In a few cases, a further complication arises.  The duration of the fault depends on the type of protection scheme used, the location of the fault and the choice of using primary or back-up clearing times for the fault (shock) duration.  The fault duration not only affects the decrement factor Df, but also the tolerable voltages, as discussed in clause 8.  If the fault clearing time for a particular fault is relatively long, the corresponding tolerable voltages may be reduced to values that make this fault condition the worst case, even though the grid current for this case is not the maximum value.  This situation generally occurs where a delta-wye grounded transformer is fed from a relatively weak source of fault current and the fault occurs some distance down a rural distribution feeder.  In this case, the high (delta) side fault current may be relatively low, and the low (wye grounded) side feeder faults are determined primarily by the transformer and feeder impedances.  If back-up clearing is considered, a feeder fault several kilometers down the feeder depending on the high side clearing device to back-up the failure of the feeder breaker could take several seconds to clear.  The tolerable voltage for this case may be significantly lower than that for a high side fault, making the low side feeder fault the worst case for the grid design.  Thus, the worst fault type and location must take into consideration not only the maximum value of grid current IG, but also the tolerable voltages based on the fault clearing time.

15.9  Computation of current division - step (b)

For the assumption of a sustained flow of the initial ground fault current, the symmetrical grid current can be expressed as:





(68)

To determine Ig, the current division factor Sf  must be computed.

The process of computing consists of deriving an equivalent representation of the overhead ground wires, neutrals, etc., connected to the grid and then solving the equivalent to determine what fraction of the total fault current flows between the grid and earth, and what fraction flows through the ground wires or neutrals.  Sf  is dependent on many parameters, some of which are:

a) Location of the fault, as described in 15.8

b) Magnitude of substation ground grid impedance, as discussed in clause 4.

c) Buried pipes and cables in the vicinity of or directly connected to, or both, the substation ground system, as discussed in 15.7

d) Overhead ground wires, neutrals, or other ground return paths, as discussed in 15.6
Because of Sf, the symmetrical grid current Ig, and therefore also IG, are closely related to the location of the fault.  If the additional ground paths of item (c) and (d) above are neglected, the current division ratio (based on remote versus local current contributions) can be computed using traditional symmetrical components.  However, the current Ig, computed using such a method may be overly pessimistic, even if the future system expansion is taken into consideration.

The remaining discussion refers only to overhead ground wires and neutral conductors, although the principles involved also apply to buried pipes, cables, or any other conducting path connected to the grid.  High‑voltage transmission lines are commonly provided with overhead static wires, either throughout their length or for short distances from each substation.  They may be grounded at each tower along the line or they may be insulated from the towers and used for communication purposes.  There are many bibliographic sources that provide assistance in determining the effective impedance of a static wire as seen from the fault point. [B20], [B21], [B22], [B25], [B50], [B87], [B112], [B147]  Many of these methods may, however, be difficult to apply by the design engineer.  Because it is beyond the scope of this guide to discuss in detail the applicability of each method to all possible system configurations, only a brief description of some of the more recent methods win be given.

Endrenyi presents an approach in which, for a series of identical spans, the tower impedances and overhead ground wires or neutrals are reduced to an equivalent lumped impedance. [B55], [B56]  Except for estimating purposes, Endrenyi recommends including the mutuals between multiple ground conductors and introduces a coupling factor to account for the mutual impedance between the neutral conductors and the phase conductors.  This technique is developed further by Verma and Mukhedkar. [B147]

In the cascaded matrix method of Sebo [B123], an impedance matrix is derived for each span of the line, and the individual span matrices are cascaded into a resulting matrix representing the entire line.  This technique allows one to take into account all self and mutual impedances (except between the tower footing grounds), and the location and type of fault.  A correction for the end effects of the line is suggested, using a modified screening factor.

With some limitations in applicability and accuracy, the span‑by‑span calculation technique can be considerably simplified.  A typical approach, in which all mutual couplings between the neutral conductor and phase conductors and between neutral conductors are ignored, has been described by Garrett. [B68]  In this technique, each neutral conductor is modeled by the impedance of each span and the equivalent ground impedance of each tower to form a network resembling a ladder.  This ladder network is then reduced, using simple network reduction techniques, to an input impedance as seen from the fault point.  The input impedance of each circuit is combined with the grid resistance and three times this resulting value is included in the zero‑sequence equivalent fault impedance.  The current division factor Sf is computed by applying Kirchoff's current law to obtain the current division between the grid resistance and the input impedance of each circuit.  Although this, or similar approximate approaches, is limited in applicability and accuracy, in many cases it may provide a reasonable estimate of the influence of overhead ground wires and neutrals on both the resistance of the grounding system and the current division ratio.

Dawalibi [B39] provides algorithms for deriving simple equations to solve for the currents in the grid and in each tower.  These equations are obtained from one or both ends of each line and do not require the large computer storage requirements of the techniques that model each span individually.  Dawalibi also addresses the effects of the soil structure (that is, multilayer earth resistivities) on the self and mutual impedances of the conductors and on the current division ratio.

Meliopoulos et al. [B93] introduce an equivalent conductor to represent the effects of earth using Carson's formula.  Every span in each line is modeled and the resulting network is solved for current flows.  From this solution, the current division ratio is computed.  The number of lines and substations modeled are limited only by the computer used to solve the network.

Garrett and Patel [B???] used the method of Meliopoulos [B93] to perform a parametric analysis of the parameters affecting Sf, and to develop a set of curves of Sf vs. grid resistance for some of the most critical parameters.  This provides a quick and simple method to estimate the current division that avoids the need for some of the simplifying assumptions of the other approximate methods, though the results are still only approximate.  These curves, along with a few new curves added for this guide, are included in annex C.

Obviously, the techniques that model the static wires, phase conductors, towers, etc., in detail will give the best evaluation of the current division ratio Sf.  However, the approximate methods discussed above have been compared with the detailed methods and found to give comparable answers for many simple examples.  Thus, the choice of the method used to determine Sf  will depend on the complexity of the system connected to the substation and the desired degree of accuracy.  A simple example follows, showing the results of four of the methods described above.  In the following example, Endrenyi's and Garrett/Patel's approximate methods are compared with the results of Dawalibi's and Meliopoulos' more accurate methods.

Example:  Figure 15-5 shows a one feeder distribution substation fed by single transmission line connecting the substation to a remote equivalent source (next adjacent substation).  The transmission line is 20 km long and the distance between tower grounds is 0.5 km.  The feeder is 4 km long and the distance between pole grounds is 0.122 km.  The soil is assumed to be uniform with a resistivity of 200 ‑m.  Carson's equations (reference) are used to compute the self impedances of the phase conductors and overhead static wire, and the mutual impedance between these (transmission line only) for use with Endrenyi's formula and Garrett/Patel's split-factor curves.  Annex C shows the equations used to calculate the line impedances necessary for the current split computations.  The various impedances for each line section tower footing resistance, remote terminal ground resistance, and substation grid resistance are:

Rtl
= 10.0 + j0.0 /section

Rtf
= 25.0 + j0.0 /section

Rs
= 3.0 + j0.0 
Rg
= 2.5 + j0.0 
Z1
= 3.82 + j9.21  for the 115 kV line

Z0(a)
= 7.37 + j35.86  for the 115 kV line

Z0(g)
= 148.24 + j66.44  for the 115 kV line

Z0(ag)
= 3.56 + j33.34  for the 115 kV line

Z0
= 12.54 + j39.72  for the 115 kV line

Zs-l
= 1.24 + j0.55 /span for the 115 kV overhead static wire

Zs-f 
= 0.11 + j0.11 /span for the 12.47 kV feeder neutral

where

Rtl
is the impedance to remote earth of each transmission tower ground electrode, 

Rtf
is the impedance to remote earth of each distribution pole ground electrode,  

Rs 
is the remote terminal ground impedance (equivalent),  

Rg
is the station ground impedance to remote earth,  

Z1
is the equivalent positive sequence impedance for the 115 kV line,  

Z0(a)
is the zero sequence self impedance for the 115 kV phase conductors,  

Z0(g)
is the zero sequence self impedance for the 115 kV ground wire,  

Z0(ag)
is the zero sequence mutual impedance between phase and ground conductors for the 115 kV line,  

Z0
is the equivalent zero sequence impedance for the 115 kV line,  

Zs-l
is the self impedance of the 115 kV overhead static wire, /span

Zs-f
is the self impedance of the 12.47 kV feeder neutral, /span

Adding the 115 kV line impedances to the source impedances gives the following equivalent fault impedance at the 115 kV bus:

Z1(eq)
= 3.82 + j19.01 
Z0(eq)
= 12.54 + j46.32 
Thus, for a 115 kV single-line-to-ground fault,



 A

Figure 15-5 {revise old fig25}
Figure 15-5

Example system for computation of current division factor Sf  

As shown in the figure, a single-line-to-ground fault occurs at the substation from the phase conductor bus to the substation neutral.

Using Endrenyi's method described in [B55], the equivalent impedance of the overhead static wire (as seen from the fault point and ignoring the effects of coupling) is:



 
The equivalent impedance of the feeder neutral (as seen from the substation) is:



 
The resulting equivalent of the overhead static wire and feeder neutral is found by paralleling the above equivalent impedances:



 (
The current division factor, Sf, is




and the resulting grid current Ig is



 A

Using Garrett and Patel's table of split factor equivalents (annex C), the equivalent of the overhead static wire and feeder neutral is

Zeq = 0.91+j 0.485 
and the split factor is




Thus, the grid current is



 A

Using Garrett/Patel's split factor curves (annex C, figure C3), the approximate split factor Sf = 0.28.  Thus, the grid current is



 A

Using Meliopoulos' algorithm [B??](???ref - EPRI Report TR-100622, Project 1494-2, May 1992  Substation Grounding Programs, Volume 2: Smecc Version 2.4), the total fault current 3I0 is 2471.5 A.  Approximately 34 percent (Ig = 835.9 A) of the fault current flows through grid to remote earth, so the current division factor equals 0.34.  Dawalibi's algorithm [B39] gives similar results.

As shown above, the approximate and detailed methods are in close agreement for this example.  However, for more complex systems, with both local and remote ground sources and with dissimilar lines and sources, the results may not be in close agreement.
15.10  Effect of asymmetry - step (c)

The maximum grid current, IG, as described in 15.2 and 15.3, is the maximum asymmetrical ac current that will flow between the grounding grid and surrounding earth.  This asymmetrical current, defined by equation (62), includes the symmetrical ac current, Ig, as well as a correction for a dc component.  The dc component decays exponentially and is known as the dc offset current.  Becuse the design of a grounding grid must consider the asymmetrical current, a decrement factor, Df, will be derived to take into account the effect of dc current offset.

In general, the asymmetrical fault current includes the subtransient, transient and steady‑state ac components, and the dc offset current component.  Both the subtransient and transient ac components and the dc offset decay exponentially, each having a different attenuation rate.

However, in typical applications of this guide, it is assumed that the ac component does not decay with time, but remains at its initial value. Thus, as a periodic function of time t, the asymmetrical fault current may be expressed as





(69)

where

if(t)
is the asymmetrical fault current, in A, at any instant t, t in s

E
is the prefault rms voltage, line-to-neutral V


is the system frequency in rad/s


is the voltage angle at current initiation in radians

(
is the circuit phase angle in rads

Yac
is the equivalent ac system admittance in mhos

Ta
is the dc offset time constant in s (Ta = X/(R, for 60 Hz, Ta = X/120(R)

The X/R ratio to be used here is the system X/R ratio at the fault location for a given fault type.  The X and R components of the system subtransient fault impedance should be used to determine the X/R ratio.

In reality, faults occur at random with respect to the voltage wave.  However, the shock contact may exist at the moment the fault is initiated.  Hence, to allow for the most severe condition, it is necessary to assume that the maximum possible dc offset will be present at the moment of an accidental shock contact.

Maximum dc offset occurs when: ( - () = -(/2

Then equation (69) becomes





(70)

Because the experimental data in the fibrillation threshold are based on the energy content of a symmetrical sine wave of constant amplitude, it is necessary to establish an equivalent rms value of the asymmetrical current wave for the maximum time of possible shock exposure.  This value, in accordance with the definition of the effective asymmetrical fault current IF, can be determined by integration of equation (70) squared over the entire duration interval of fault tf  in s.





(71)

where

IF
is the effective rms value of approximate asymmetrical current for the entire duration of a fault

tf
is the time duration of fault in s

t
is the time (variable) after the initiation of fault in s

Evaluating the integral of equation (71) in terms of equation (70), it follows that





(72)

Therefore, the decrement factor Df is determined by the ratio IF/If, yielding,





(73)





(74)

Equation (74) can be used to compute the decrement factor for specific X/R ratios and fault durations.  Typical values of the decrement factor for various fault durations and X/R ratios are shown in table 15-1.

For relatively long fault durations, the effect of the dc offset current can be assumed to be more than compensated by the decay of the subtransient component of ac current.  A decrement factor of 1.0 can be used for fault durations of 30 cycles or more.

For closely spaced successive shocks (possibly from reclosures), early editions of this guide suggested a decrement factor computed using the shortest single fault duration, even if the time ts used elsewhere in the calculations is based on the sum of the individual shock durations.  However, the preceding discussion of the asymmetrical fault current decrement factor suggests that the use of the shortest fault duration in conjunction with the longest shock duration, or sum of the shock durations, may result in an over designed grounding system.  This is especially true for faults of intermediate duration (that is, 6 to 30 cycles), where the decrement factor is relatively large and the ac component of current is assumed to remain at its subtransient value.  Crawford and Griffith [B24] suggest that the shock duration and fault duration be assumed identical, which will result in sufficient grid design for cases involving no automatic reclosures or successive (high‑speed) shocks.  However, because little or no testing has been done on the effects of repetitive shocks separated by only a few cycles, the design engineer should judge whether or not he should use the longest shock duration for time ts" elsewhere in the calculations and the shortest fault duration for the time tf in computing the decrement factor with equation (74).

NOTE: It is important that the values of the decrement factor given in table 15-1 not be confused with the multiplying factors given by IEEE C37.010‑1979.  The decrement factor is Df, and is used to determine the effective current during a given time interval after inception of a fault, whereas the multiplying factors given by IEEE C37.010‑1979 are used to determine the rms current at the end of this interval.  Because of the decay of ac and dc transient components with time, the decrement factors determined by equation (74) are slightly higher than the factors given by IEEE C37.010-1979 for short fault and shock durations.

15.11  Effect of future changes - step (d)

It is a common experience for maximum fault currents at a given location to increase as system capacity is added or new connections are made to the grid.  While an increase in system capacity will increase the maximum expected fault current IF, new connections may increase or decrease the maximum grid current IG.  One case in which the grid current may decrease with new connections is when new transmission lines are added with ground or neutral wires, or both.  In general, if no margin for increase in IG is included in the original ground system design, the design may become unsafe.  Also, subsequent additions will usually be much less convenient and more expensive to install.  It has been a widely accepted practice to assume the total fault current, IF, between the grid and surrounding earth (that is, ignoring any current division) in an attempt to allow for system growth.  While this assumption would be overly pessimistic for present year conditions, it may not exceed the current IG computed considering current division and system growth.  If the system growth is taken into account and current division is ignored, the resulting grid will be overdesigned.  An esti​mate of the future system conditions can be obtained by including all system additions forecasted.

Caution should be exercised when future changes involve such design changes as disconnection of overhead ground wires coming into the substations.  Such changes may have an effect on ground fault currents, resulting in an inadequate grounding system.  However, future changes such as additions of incoming over​head ground wires may decrease the current division ratio, resulting in the existing ground system being, in effect, overdesigned.

Table 15-1

Typical values of Df



Decrement factor Df

Fault
duration 
tf (s)
Cycles

at 60 Hz
X/R = 10
X/R = 20
X/R = 30
X/R = 40

0.008 33
0.5
1.576
1.648
1.675
1.688

0.05
3
1.232
1.378
1.462
1.515

0.10
6
1.125
1.232
1.316
1.378

0.20
12
1.064
1.125
1.181
1.232

0.30
18
1.043
1.085
1.125
1.163

0.40
24
1.033
1.064
1.095
1.125

0.50
30
1.026
1.052
1.077
1.101

0.75
45
1.018
1.035
1.052
1.068

1.00
60
1.013
1.026
1.039
1.052

16.  Design of grounding system
16.1  Design criteria
As stated in 4.1, there are two main design goals to be achieved by any substation ground system under normal as well as fault conditions.  These goals are (1) to provide means to dissipate electric currents into the earth without exceeding any operating and equipment limits, and (2) to assure that a person in the vicinity of grounded facilities is not exposed to the danger of critical electric shock.

The design procedures described in the following sections are aimed at achieving safety from dangerous step and touch voltages within a substation.  It is pointed out in 8.2 that it is possible for transferred potentials to exceed the GPR of the substation during fault conditions.  Clause 17 discusses some of the methods used to protect personnel and equipment from these transferred potentials.  Thus, the design procedure described here is based on assuring safety from dangerous step and touch voltages within, and immediately outside, the substation fenced area.  Because the mesh voltage is usually the worst possible touch voltage inside the substation (excluding transferred potentials), the mesh voltage will be used as the basis of this design procedure.

Step voltages are inherently less dangerous than mesh voltages.  If, however, safety within the grounded area is achieved with the assistance of a high resistivity surface layer (surface material), which does not extend outside the fence, then step voltages may be dangerous.  In any event, the computed step voltages should be compared with the permissible step voltage after a grid has been designed that satisfies the touch voltage criterion.

For equally spaced ground grids, the mesh voltage will increase along meshes from the center to the corner of the grid.  The rate of this increase will depend on the size of the grid, number and location of ground rods, spacing of parallel conductors, diameter and depth of the conductors, and the resistivity profile of the soil.  In a computer study of three typical grounding grids in uniform soil resistivity, the data shown in table 16-1 were obtained.  These grids were all symmetrically shaped square grids with no ground rods and equal parallel conductor spacing.  The corner Em was computed at the center of the  corner mesh.  The actual worst case Em occurs slightly off-center (toward the corner of the grid), but is only slightly higher than the Em at the center of the mesh.

As indicated in table 16-1, the corner mesh voltage is generally much higher than that in the center mesh.  This will be true unless the grid is unsymmetrical (that is, has projections, or L-shaped, etc.), has ground rods located on or near the perimeter, or has extremely non uniform conductor spacings.  Thus, in the simplified equations for the mesh voltage Em given in 16.5, only the mesh voltage at the center of the corner mesh is used as the basis of the design procedure.
  Analysis based on computer programs, described in 16.8, may use this approximate corner mesh voltage, the actual corner mesh voltage, or the actual worst‑case touch voltage found anywhere within the grounded area as the basis of the design procedure.  In either case, the initial criterion for a safe design is to limit the computed mesh or touch voltage to below the tolerable touch voltage from equation (32a) or (32b).

Table 16-1

Typical ratio of corner-to-center mesh voltage

Grid Number
Grid Size (Meshes*Meshes)
Em Corner/Center

1
10 x 10
2.71

2
20 x 20
5.55

3
30 x 30
8.85

16.2  Critical parameters
The following site‑dependent parameters have been found to have substantial impact on the grid design: maximum grid current IG, fault duration tf, shock duration ts, soil resistivity s), and grid geometry.  Several parameters define the geometry of the grid, but the area of the grounding system, the conductor spacing, and the depth of the ground grid have the most impact on the mesh voltage, while parameters such as the conductor diameter and the thickness of the surfacing material have less impact. [B1], [B40], [B43], [B127]  A brief discussion or review of the critical parameters is given below.
, high resistivity surface material (
16.2.1  Maximum grid current (IG)
The evaluation of the maximum design value of ground fault current that flows through the substation grounding grid into the earth, IG, has been described in clause 15.  In determining the maximum current IG, by means of equation (62), consideration should be given to the resistance of the ground grid, division of the ground fault current between the alternate return paths and the grid, and the decrement factor.

16.2.2  Fault duration (tf) and shock duration (ts)

The fault duration and shock duration are normally assumed equal, unless the fault duration is the sum of successive shocks, such as from reclosures.  The selection of tf, should reflect fast clearing time for transmission substations and slow clearing times for distribution and industrial substations.  The choices tf and ts should result in the most pessimistic combination of fault current decrement factor and allowable body current.  Typical values for tf and ts range from 0.25 to 1.0 s.  More detailed information is given in 5.2 to 6.4 and 15.10 on the selection of tf and ts.

16.2.3  Soil resistivity ()

The grid resistance and the voltage gradients within a substation are directly dependent on the soil resistivity.  Because in reality soil resistivity will vary horizontally as well as vertically, sufficient data must be gathered for a substation yard.  The Wenner method described in 13.3 is the widely used. [B148], [B92]

Because the simplified equations for Em and Es given in 16.5 assume uniform resistivity soil, the equations can employ only a single value for the resistivity.  There is no simple method to determine a value from the field test data that can yield an accurate ground grid analysis using these simplified equations.  However, the following points may provide the user with general guidelines.

(1) The soil can be considered uniform if the difference between two extreme resistivity values of the field test data is 30 percent or less.  In this case a simple average of all the resistivity values can be used in equations (75) and (80).

(2) When an equivalent two‑layer soil model is determined (see 13.4.2.2) and the ground system is in the upper layer, the value of 1 is used as the soil resistivity in equations (75) and (80).
1 (upper‑layer soil resistivity) can be used in the simplified equations.  As stated in 13.6.2, for negative values of reflection factor K the grids designed using uniform soil analysis will have higher step and touch voltages than the grids designed with the equivalent two‑layer model, if 
16.2.4  Resistivity of surface layer (s)

A thin surface layer of surface material helps in limiting the body current by adding resistance to the equivalent body resistance.  Values from 1000 to 5000 s.  Refer to 7.4 and 12.5 for more details on the application of this parameter.
‑m have been used for 
16.2.5  Grid geometry

In general, the limitation on the physical parameters of a ground grid are based on economics and the physical limitations of the installation of the grid.  The economic limitation is obvious.  It is impractical to install a copper plate grounding system.  Clause 18 describes some of the limitations encountered in the installation of a grid.  For example, the digging of the trenches into which the conductor material is laid limits the conductor spacing to approximately 2 m or more.  Typical conductor spacings range from 3 to 15 m, while typical grid depths range from 0.5 to 1.5 m.  For the typical conductors ranging from AWG 2/0 to 500 kcmils, the conductor diameter has negligible effect on the mesh voltage.  The area of the grounding system is the single most important geometrical factor in determining the resistance of the grid.  The larger the area grounded, the lower the grid resistance and, thus, the lower the GPR.

16.3  Index of design parameters
Table 16-2 contains a summary of the design parameters used in the design procedure.

Table 16-2

Index of design parameters

                                                                                                                                         NEED TO REVISE REFERENCE CLAUSE

Symbol
Description
Reference Clauses

3I0
Symmetrical fault current in substation for conductor sizing, A
9.3, 9.4, 13.2, 13.4

IG
Maximum grid current that flows between ground grid and surrounding earth (including dc offset), A
13.4


Soil resistivity, -m
11

s
Surface layer resistivity, -m
5.4, 10.5

hs
Surface layer thickness, m
5.4

Cs
Surface layer derating factor
5.4

tc
Duration of fault current for sizing ground conductor, s
13.1, 13.10

tf
Duration of fault current for determining decrement factor, s
13.9

ts
Duration of shock for determining allowable body current, s
3.2-4.3

h
Depth of ground grid conductors, m
12.2, 12.3

d
Diameter of grid conductor, m
9.3, 9.4, 9.6

A
Total area enclosed by ground grid, m2
12.2, 12.3

D
Spacing between parallel conductors, m
14.4, 14.5

Df
Decrement factor for determining IG
13.1, 13.9, 14.2

n
Geometric factor composed of factors na, nb, nc, and nd
14.4, 14.5

Km
Spacing factor for mesh voltage, simplified method
14.4, 14.5

Ks
Spacing factor for step voltage, simplified method
14.4, 14.5

Ki
Correction factor for grid geometry, simplified method
14.4, 14.5

Kii
Corrective weighting factor that adjusts for the effects of inner conductors on the corner mesh, simplified method
14.5, A

Kh
Corrective weighting factor that emphasizes the effects of grid depth, simplified method
14.5, A

LT
Total effective length of grounding system conductor, including grid and ground rods, m
14.5

Lc
Total length of grid conductor, m
14.5

LR
Total length of ground rods, m
14.5

Lr
Length of ground rod at each location, m
14.5

Lm
Effective length of  Lc + LR for mesh voltage


Ls
Effective length of  Lc + LR for step voltage


Lx
Maximum length of grid conductor in x direction


Ly
Maximum length of grid conductors in y direction


Lr
Perimeter length of grid conductors


nr
Number of rods


Rg 
Resistance of grounding system, 
12.1-12.4

Em
Mesh voltage at the center of the corner mesh for the simplified method, V
14.4, 14.5

Es
Step voltage between a point above the outer corner of the grid and a point 1 m diagonally outside the grid for the simplified method, V
14.4, 14.5

Etouch50
Tolerable touch voltage for human with 50 kg body weight, V
6.2, 6.3

Etouch70
Tolerable touch voltage for human with 70 kg body weight, V
6.2, 6.3

Estep50
Tolerable step voltage for human with 50 kg body weight, V
6.2

Estep70
Tolerable step voltage for human with 70 kg body weight, V
6.2

16.4  Design procedure
The block diagram of figure 16-1 illustrates the sequences of steps to design the ground grid.  The parameters shown in the block diagram are identified in the index presented in table 16-2 of 16.3.  The following describes each step of the procedure:

Step 1)
The property map and general location plan of the substation should provide good estimates of the area to be grounded.  A soil resistivity test, described in clause 13, will determine the soil resistivity profile and the soil model needed (that is, uniform or two-layer model).

Step 2)
The conductor size is determined by equations given in 11.3.  The fault current 3I0 should be the maximum expected future fault current that will be conducted by any conductor in the grounding system, and the time ts should reflect the maximum possible clearing time (including back‑up).

Step 3)
The tolerable touch and step voltages are determined by equations given in 8.3 and 8.4. The choice of time ts is based on the judgment of the design engineer, with guidance from 5.2 to 6.3.

Step 4)
The preliminary design should include a conductor loop surrounding the entire grounded area, plus adequate cross conductors to provide convenient access for equipment grounds, etc.  The initial estimates of conductor spacing and ground rod locations should be based on the current IG and the area being grounded.

Step 5)
Estimates of the preliminary resistance of the grounding system in uniform soil can be determined by the equations given in 14.2 and 14.3.  For the final design, more accurate estimates of the resistance may be desired.  Computer analysis based on modeling the components of the grounding system in detail can compute the resistance with a high degree of accuracy, assuming the soil model is chosen correctly. 

Step 6)
The current IG is determined by the equations given in clause 15.  In order to prevent gross over‑design of the grounding system, only that portion of the total fault current 3I0, that flows through the grid to remote earth (and contributes to the mesh and step voltages and the GPR) should be used in designing the grid.  The current IG should, however, reflect the worst fault type and location, the decrement factor, and any future system expansion.

Step 7)
If the GPR of the preliminary design is below the tolerable touch voltage, no further analysis is necessary.  Only additional conductor required to provide access to equipment grounds is necessary.

Step 8)
The calculation of the mesh and step voltages for the grid as designed can be done by the approximate analysis techniques described in 16.5 for uniform soil, or by the more accurate computer analysis techniques, as demonstrated in 16.8.  Further discussion of the calculations are reserved for those sections.

Step 9)
If the computed mesh voltage is below the tolerable touch voltage, the design may be complete [see step (10)].  If the computed mesh voltage is greater than the tolerable touch voltage, the preliminary design should be revised [see step (11)].

Step 10)
If both the computed touch and step voltages are below the tolerable voltages, the design needs only the refinements required to provide access to equipment grounds.  If not, the preliminary design must be revised [see step (11)].

Step 11)
If either the step or touch tolerable limits are exceeded, revision of the grid design is required.  These revisions may include smaller conductor spacings, additional ground rods, etc.  More discussion on the revision of the grid design to satisfy the step and touch voltage limits is given in 16.6.

Step 12)
After satisfying the step and touch voltage requirements, additional grid and ground rods may be required.  The additional grid conductors may be required if the grid design does not include conductors near equipment to be grounded.  Additional ground rods may be required at the base of surge arresters, transformer neutrals, etc.




Figure 16-1  Design procedure block diagram

16.5  Calculation of maximum step and mesh voltages
Computer algorithms for determining the grid resistance and the mesh and step voltages have been developed in numerous recent references. [B2], [B42], [B69], [B74], [B80]  These algorithms required considerable storage capability and were relatively expensive to execute, but improvements in the solution algorithms and the proliferation of powerful desktop computers have alleviated most of these concerns.

In some cases, it is not economically justifiable to use these computer algorithms, or the designer may not have access to a  computer with the required capabilities.  This subclause, in conjunction with annex D, describes approximate equations for determining the design parameters and establishing corresponding values of Em and Es without the necessity of using a computer.

16.5.1  Mesh voltage (Em)

The mesh voltage values are obtained as a  product of  the geometrical factor Km, a corrective factor Ki, which accounts for some of the error introduced by the assumptions made in deriving Km, the soil resistivity (), and the average current per unit of effective buried length of the grounding system conductor (IG/LM):





(75)

The components Km , Ki  and LM are computed as follows:





(76)

where






for grids with ground rods along the perimeter, or for grids with ground rods in the grid corners, as well as both along the perimeter and throughout the grid area

or



 

for grids with no ground rods or grids with only a few ground rods, none located in the corners or on the perimeter.






ho = 1m (grid reference depth)









LC
is the total length of the conductor in the horizontal grid, m

Lp
is the peripheral length of the grid, m

A 
is the area of the grid, m2
Lx
is the maximum length of the grid in the x direction, m

Ly
is the maximum length of the grid in the y direction, m

Dm
is the maximum distance between any two points on the grid, m

and D, h, and d are defined in table 16-2.





(77)

where n is as defined as above.  The effective number of parallel conductors in the grid n accounts for irregularly shaped grids.[B???Thapar ref]

For grids with no ground rods, or grids with only a few ground rods scattered throughout the grid, but none located in the corners or along the perimeter of the grid, the effective buried length, LM , is:





(78)

where

LR
is the total length of all ground rods

For grids with ground rods in the corners, as well as along the perimeter and throughout the grid, the effective buried length, LM , is:

 



(79)

where 


Lr
=
length of each ground rod in m 


and LC  and LR  are as defined above.

16.5.2  Step voltage (Es)

The step voltage values are obtained as a  product of  the geometrical factor Ks, the corrective factor Ki, the soil resistivity (), and the average current per unit of buried length of grounding system conductor (IG/LS):





(80)

For grids with or without ground rods, the effective buried conductor length, LS , is:





(81)

The maximum step voltage is assumed to occur over a distance of 1 meter, beginning at and extending  outside of the perimeter conductor at the angle bisecting the most extreme corner of the grid.  For the usual burial depth  of 0.25 m < h < 2.5 m





(82)

16.6  Refinement of preliminary design
If calculations based on the preliminary design indicate that dangerous potential differences can exist within the substation, the following possible remedies should be studied and applied where appropriate.

a) Decrease total grid resistance:  A decrease in total grid resistance will decrease the maximum GPR and hence the maximum transferred voltage.  The most effective way to decrease ground grid resistance is by increasing the area occupied by the grid.  Deep driven rods or wells may be used if the available area is limited.  A decrease in substation resistance may or may not decrease appreciably the local gradients, depending on the method used.

b) Closer grid spacings:  By employing closer spacing of grid conductors, the condition of the continuous plate can be approached more closely.  Dangerous potentials within the substation can thus be eliminated at a cost.  The problem at the perimeter may be more difficult, especially at a small substation when resistivity is high.  However, it is usually possible, by burying the grid ground conductor outside the fence line, to ensure that the steeper gradients immediately outside this grid perimeter do not contribute to the more dangerous touch contacts.  Another effective and economical way to control gradients is to increase the density of ground rods at the perimeter. This density  may be decreased toward the center of the grid. Another approach to controlling perimeter gradients and step potentials is to bury two or more parallel conductors around the perimeter at successively greater depth as distance from the substation is increased. [B1], [B10], [B87]

c) Diverting a greater part of the fault current to other paths:  By connecting overhead ground wires of transmission lines or by decreasing the tower footing resistances in the vicinity of the substation, part of the fault current will be diverted from the grid.  In connection with the latter, however, the effect on fault gradients near tower footings should be weighed.

d) Limiting total fault current:.  If feasible, limiting the total fault current will decrease the GPR and all gradients in proportion.  Other factors, however, will usually make this impractical.  Moreover, if accomplished at the expense of greater fault clearing time, the danger may be increased rather than diminished.

e) Barring access to limited areas:  Barring access to certain areas, where practical, will reduce the probability of hazards to personnel.

16.7  Application of simplified equations for Em and Es
Several simplifying assumptions are made in deriving the equations for Em and Es.  The equations were compared with more accurate computer results from cases with various grid shapes, mesh sizes, numbers of ground rods, and lengths of ground rods, and found to be consistently better than the previous equations.  These cases included square, rectangular, triangular, T-shaped, and L-shaped grids.  Cases were run with and without ground rods.  The total ground rod length was varied with different numbers of ground rod locations and different ground rod lengths.  The area of the grids was varied from 6.25 to 10 000 m2 .  The number of meshes along a side was varied from 1 to 40.  The mesh size was varied from 2.5 to 22.5 m2.  All cases assumed a uniform soil model and uniform conductor spacing.  Most practical examples of grid design were considered.  The comparisons found the equations to track the computer results with acceptable accuracy. 

16.8  Use of computer analysis in grid design
There are several reasons that may justify the use of more accurate computer algorithms in designing the grounding system.  These reasons include:

a) Parameters exceed those of the test cases described above. 

b) A two‑layer or multi-layer soil model is required due to significant variations in soil resistivity

c) Uneven grid conductor or ground rod spacings cannot be analyzed using the approximate methods of 16.5

d) More flexibility in determining local danger points may be desired

e) Several references describe computer algorithms for modeling grounding systems. [B2], [B42], [B74]  In general, these algorithms are based on (1) modeling the individual components comprising the grounding system (that is, grid conductors, ground rods, etc.), (2) forming a set of equations describing the interaction of these components, (3) solving for the ground‑fault current flowing from each component into the earth, and (4) computing the potential at any desired surface point due to all the individual components.

The accuracy of these computer algorithms depends mostly on the size and number of segments each component is broken into for modeling.  This determines the accuracy of the current density computed for each conductor segment.  Of course, the accuracy of both the computer algorithms and approximate equations of 16.5 also depends on other parameters, such as the soil model and resistivity value.

17.  Special areas of concern

Before the final grounding grid design calculations are completed, there still remains the important task of investigating possible special areas of concern in the substation grounding network.  This includes an investigation of grounding techniques for substation fence, switch operating shafts, rails, pipelines, and cable sheaths.  The effects of transferred potentials should also be considered.

17.1  Service areas

The problems associated with step and touch voltage exposure to persons outside a substation fence are much the same as those to persons within fenced substation areas .

Occasionally, a fence will be installed to enclose a much larger area than initially utilized in a substation and a grounding grid will be constructed only in the utilized area and along the substation fence.  The remaining unprotected areas within the fenced area are often used as storage, staging, or general service areas.  Temporary grounding is often used in service areas.

A reduced substation grid, which does not include the service area, has both initial cost advantages and future savings resulting from not having the problems associated with "working around" a previously installed total area grid system when future expansion is required into the service area.  However, a reduced grid provides less personnel protection compared to a complete substation grid, which includes the service area.  Also, because of the smaller area and less conductor length, a service area grid and reduced substation grid will have a higher overall resistance compared to a complete substation grid, which includes the service area.

17.2  Switch shaft and operating handle grounding

Operating handles of switches represent a significant concern if the handles are not adequately grounded.  Because the manual operation of a switch requires the presence of an operator near a grounded structure, several things could occur which may result in an arc to the structure, thus subjecting the operator to an electrical shock.  This includes the opening in error of an energized circuit, mechanical failure, electrical breakdown of a switch insulator or attempting to interrupt a  greater value of line charging current or transformer magnetizing current than the switch can safely interrupt.

It is relatively easy to protect against these hazards when the operating handle is within a reasonably extensive substation ground grid area.  If the grounding system has been designed in accordance with this standard, touch and step voltages near the operating handle should be within safe limits.  However, quite often additional means are taken to provide a greater safety factor for the operator.  For example, one might connect the switch operating shaft to a ground mat or mesh which the operator stands on when operating the switch.  The ground mat is connected directly to the ground grid and the switch operating shaft.  This technique provides a direct bypass to ground across the person operating the switch.  Of course, the grounding wires must be adequately sized to carry the ground fault current for the required duration.  An undersized ground wire could burn open under a fault condition, thus subjecting the switch operator to the ground fault current.  Fatal accidents have occurred as a result of this.  Refer to figure 17-1 for a typical switch shaft grounding practice.

The practices for grounding switch operating shafts are varied.  The results of a questionnaire issued in 1985 indicated that 78 out of 79 utilities that responded required grounding of substation air switch operating shafts to the grounding grid.  The methodology for accomplishing this grounding was almost equally divided amongst those responding to the questionnaire.  Approximately half of the utilities provided a direct jumper between the switch shaft and the ground mat, while the other half provided a jumper from the switch shaft to the adjacent grounded structural steel.  The steel is used as part of the conducting path. Approximately 90 percent of the utilities utilized a braid for grounding the switch shaft. The remaining 10 percent utilized a braidless grounding device. A typical braided ground is shown in figure 17-2 and a braidless grounding device is shown in figure 17-3.

17.3  Grounding of substation fence

Fence grounding is of major importance because the fence is usually accessible to the general public and the hazard involved is that of dangerous touch potential.  Step potential is usually not a concern at the fence perimeter, but should be checked to verify that a problem does not exist.  The substation grounding design should be such that the touch potential on the fence is within the calculated tolerable limit of touch potential.

Several philosophies exist with regard to grounding of substation fence.  The National Electrical Safety Code C2-1993 requires that metal fences used to enclose electric supply substations having energized electrical conductors or equipment shall be grounded.  This fence grounding requirement may be accomplished by bonding the fence to the substation grounding grid or to a separate underground conductor below or near the fence line.  The various fence grounding practices are:

- Fence is within the ground grid area and is connected to the substation ground grid.

- Fence is outside of ground grid area and is connected to the substation ground grid.

- Fence is outside of ground grid area, but is not connected to the substation ground grid.  Fence is connected to a separate grounding conductor.

- Fence is outside of ground grid area, but is not connected to the substation ground grid. Fence is not connected to a separate grounding conductor.  The contact of the fence post through the fence post concrete to earth is relied on for an effective ground.

If the latter two practices on fence grounding are to be followed, i.e., if the fence and its associated grounds are not to be coupled in any way to the main ground grid (except through the soil), then three factors require consideration:

- Is the falling of an energized line on the fence a danger which must be considered?

- May hazardous potentials exist at the fence during other types of faults because the fence line crosses the normal equipotential contours?

- In practice, can complete metallic isolation of the fence and substation ground grid be assured at all times?

In regard to the first factor for consideration, construction of transmission lines over private fences is common and gives no undue concern.  The number of lines crossing a substation fence may be greater, but the spans are often shorter and deadened at one or both ends.  Hence, the danger of a line falling on a fence is usually not of great concern.  If one is to design against this danger, then very close coupling of the fence to adjacent ground throughout its length is necessary.  Touch and step potentials on both sides of the fence must be within the acceptable limit for a short-circuit current of essentially the same maximum value as for the substation.  This is somewhat impractical because the fence is not tied to the main ground grid in the substation and the adjacent earth would be required to dissipate the fault current through the local fence grounding system.

In regard to the second factor for consideration, fences do not follow the normal equipotential lines on the surface of the earth which result from fault current flowing to and from the substation grounding grid.  If coupling of the fence to ground is based solely on the contact between the fence posts and the surrounding earth, the fence might, under a fault condition, attain the potential of the ground where the coupling was relatively good, and thereby attain a high voltage in relation to the adjacent ground surface at locations where the coupling was not as good.  The current flowing in the earth and fence, and the subsequent touch voltage on the fence are less than would result from an energized line falling on the fence; however, the touch voltage may exceed the allowable value and would hence be unsafe.

In regard to the third factor for consideration, it may be somewhat impractical to expect complete metallic isolation of the fence and the substation ground grid.  The chance of an inadvertent electrical connection between the grid and the fence areas may exist.  This inadvertent electrical connection may be from metallic conduits, water pipes, etc.  These metallic items could transfer main grid potential to the fence and hence dangerous local potential differences could exist on the fence during a fault.  If the fence is not closely coupled to the nearby ground by its own adequate ground system then any such inadvertent connections to the main grid could create a hazard along the entire fence length under a fault condition.  This hazard could be only partially negated by utilizing insulated joints in the fence at regular intervals.  However, this does not appear to be a practical solution to the possible hazard.

Another disadvantage of not including the fence within the ground grid area is the reduction in the size of the ground grid area.  This will thereby increase the ground grid resistance.  The advantages of not connecting the fence to the substation ground grid are cost savings and the possibility of not subjecting someone touching the fence during a substation ground fault to a potentially dangerous touch voltage.

Several different practices are followed by various companies in regard to fence grounding.  Some companies ground only the fence posts, using various types of connectors as described elsewhere in this guide.  Other companies ground the fence posts, fabric and barbed wire.  The grounding grid should extend to cover the swing of all substation gates.  The gate posts should be securely bonded to the adjacent fence post utilizing a flexible connection.

In order to illustrate the effect of various fence grounding practices on fence touch potential, five fence grounding examples were analyzed using computer analysis. The fence grounding techniques analyzed were:

CASE 1
Inclusion of fence within the ground grid area.  The outer ground wire is 0.91 m (3 ft.) outside of the fence perimeter.  The fence is connected to the ground grid.  Refer to figures 17-4 & 17-5 for grid layout.

CASE 2
Ground grid and fence perimeter approximately coincide.  The outer ground wire is directly alongside the fence perimeter. The fence is connected to the ground grid.  Refer to figures 17-6 & 17-7 for grid layout.

CASE 3
The outer ground grid wire is 0.91 m (3 ft.) inside the fence perimeter.  The fence is connected to the ground grid. Refer to figures 17-8 & 17-9 for grid layout.

CASE 4
Ground grid is inside of fence area.  The outer ground grid wire is 6.7 m (22 ft.) inside the fence perimeter.  The fence is connected to the ground grid.  Refer to figures 17-10 & 17-11 for grid layout.

CASE 5
Ground grid is inside of fence area.  The outer ground grid wire is 6.7 m (22 ft.) inside the fence perimeter.  The fence is locally grounded but not connected to the ground grid.  Refer to figures 17-12 & 17-13 for grid layout.

The fenced area for each case is a 43.9 m (144 ft.) square.  The test calculations are based on the following parameters:

(
= 60 (-m

IG
= 5 ,000 A

hs
= 0.076 m

(s 
= 3000 (-m, extending 0.91 m (3 ft.) beyond the fence

Rg
= 0.66 ( for cases 1-4 

Rg
= 0.98 ( for case  5

ts
= 0.5 s

Df 
= 1.0

The reduction factor Cs for derating the nominal value of surface layer resistivity is dependent on the thickness of the yard stone and the reflection factor K, and is computed using and equation (23) and Figure 7-6:





 INCRUSTAR Equation.2  

The allowable step and touch voltages are calculated using equations (30a) and (32a).  For test cases 1-5:



 V



 V

The actual step voltage Es and actual mesh voltage Em are calculated as a function of the grid potential rise in percent, using the following equations; where Es ( percent) and Em ( percent) are step and mesh potentials in terms of percent of grid potential rise.







Equating the actual step and mesh voltage equations to the tolerable step and touch voltage values ( Estep = Es and Etouch = Em) and solving for Es( percent) and Em( percent), the equations become:







Substituting the assumed parameters for these test cases yields:

For cases 1-4

Es ( percent) = 60.5  percent

Em ( percent) = 18.8  percent

For case 5

Es ( percent) = 40.7  percent

Em ( percent) = 12.7  percent

The actual step and mesh voltages as a percent of grid potential rise must be less than 60.5 percent and 18.8 percent, respectively, for cases 1-4 and less than 40.7 percent and 12.7 percent, respectively, for case 5.

For each test case, two voltage profiles were computed at the following locations:

A line parallel to and 0.91 m (3 ft.) outside of fence.

A line through the grid from one side to the other, parallel to the grid wires.

17.4  Results of voltage profiles for fence grounding

The results of the voltage profiles along the surface of the earth for test case 1 are shown in figures 17-4 and 17-5.  The results for both profiles indicate that the touch potential on the fence for a person standing 0.91 m (3 ft.) from the fence (approximately one arm's length) is less than the tolerable touch voltage and hence safe.  The voltage profiles illustrate how the voltage above remote earth decreases rapidly as one leaves the substation grounding grid area.  As seen in figure 17-4, the step voltage is no greater than 3-4 percent and is far below the tolerable step voltage percent of 60.5 percent of grid potential rise.  Because step voltage is usually not the concern in regard to fence grounding, it will not be analyzed in the remaining test cases.

The results of the voltage profiles for test case 2 are shown in figures 17-6 and 17-7.  The voltage profile in figure 17-7 for a line through the grid from one side to the other indicates that the touch potential 0.91 m (3 ft.) outside of the fence is very nearly equal to the allowable touch voltage.  However, as seen in figure 17-6 for a voltage profile along the fence and 0.91 m (3 ft.) away from it, it is clear that the touch voltages on certain areas of the fence are not safe for a person to contact.  By comparing figures 17-4 and 17-6, one can clearly see the effect of having a ground grid wire 0.91 m (3 ft.) outside of the fence and around the fence perimeter.

The results of the voltage profiles for test case 3 are shown in figures 17-8 and 17-9.  These results are very similar to those of test case 2 and illustrate that the touch potential on the fence is generally not safe in several areas for a person to contact.

The results of the voltage profiles for test case 4 are shown in figures 17-10 and 17-11.  These results again illustrate that the touch potential on the fence during a fault condition is not safe to contact.  It can be seen by comparing figures 17-4, 17-6, 17-8 and 17-10 that the touch potential along the length of the fence increases as the outer ground grid wire is moved inward toward the substation.

The results of the voltage profiles for test case 5 are shown in figures 17-12 and 17-13.  The tolerable touch voltage has decreased from 18.8 percent to 12.7 percent because of an increase in the substation grid resistance.  The grid resistance increase is a result of less wire and reduced area in the grid for test case 5.  According to the computer program results, the potential rise on the isolated, separately grounded fence during a ground fault condition is 43.7 percent of grid potential rise (GPR), which is shown as a horizontal line on the graphs.  The potential rise on the fence is caused by the coupling through the earth from the ground grid to the fence.  As shown in figure 17-12, the potential rise on the earth 0.91 m (3 ft.) beyond the fence corner caused by a ground fault condition is 30.5 percent of GPR.  The largest difference in voltage between the fence and the earth occurs at the corner and is 13.2 percent of GPR, which is 0.5 percent greater than the allowable touch voltage of 12.7 percent.  It is also important to note that if the fence should ever inadvertently become metallically connected to the ground grid, the potential on the fence could reach 100 percent of GPR and the results would be similar to those shown in case 4, figures 17-10 and 17-11.

Test cases studied for an isolated ungrounded fence yield very similar results as the test cases run for an isolated, separately grounded fence shown in figures 17-12 and 17-13.

17.5  Cable sheath grounding

Metallic cable sheaths, unless effectively grounded, may attain dangerous voltages to earth.  These voltages may result from insulation failure, charges due to electrostatic induction, and flow of currents in the sheath, or from the voltage rise during faults discharging to the substation ground system to which the sheaths are connected.  All grounding connections should be made to the shield in such a way as to provide a permanent low-resistance bond.  The wire or strap used to connect the cable shield ground connection to the permanent ground must be sized to carry the available fault current.

Sheath currents on single-conductor cables can be reduced by grounding one end of the sheaths only, when the cable length is not excessive.  For long cables, the sheath should be grounded at both ends and at each splice.  Refer to IEEE Std. 525-1992.

The sheaths of shielded control cables should be grounded at both ends to eliminate induced potentials.  If the control cable sheath is grounded at widely separated points, large potential gradients in the ground grid during faults may cause excessive sheath currents to flow.  One solution is to run a separate conductor in parallel with the control cable connected to the two sheath ground points.  The current will then be diverted away from the sheath.  This separate conductor (usually bare copper) is typically routed along the top of the inside wall of the cable trench or above direct-buried conductors.

17.6  GIS bus extensions

A number of unique problems are encountered in the grounding of gas-insulated substations (GIS) vis-a-vis conventional substations.  The grounded metal enclosure of GIS equipment can be a source of dangerous touch voltages during fault conditions.  Refer to clause 10 for techniques of evaluating touch voltages in GIS.

17.7  Surge arrester grounding

Surge arresters should always be provided with a reliable low-resistance ground connection.  Arresters should be connected as close as possible to the terminals of the apparatus to be protected and have as short and direct a path to earth as practical.  While many utilities provide separate ground leads from arresters mounted on metal structures, other utilities use the arrester mounting structures as the surge arrester ground path because the large cross-section of the steel members provides a lower resistance path than a copper cable of the usual size.  In these cases it is important to insure adequate electric connections from the structure to both arrester ground lead and ground grid; and also to be sure that the steel cross-sectional area is adequate for conductivity, and that no high resistance is introduced into joints from paint films, rust, etc.

17.8  Note on separate and common grounds

The practice of having separate grounds within a substation area is rarely used for the following reasons:

a) Higher resistances for both safety (separate) and system grounds are produced than would be the case for single uniform ground system.

b) In the event of insulation failures in the substation, high currents could still flow in the safety ground.

c) Because of a high degree of coupling between separate electrodes in the same area, the safety objective (of keeping the GPR of the safety grounds low for line faults) would not be accomplished.

d) Often dangerous potentials would be possible between nearby grounded points because decoupling of the separate grounds is possible, at least to some extent.

17.9  Transferred potentials

A serious hazard may result during a ground fault from the transfer of potential between the substation ground grid area and outside locations.  This transferred potential may be transmitted by communication circuits, conduit, pipes, metallic fences, low-voltage neutral wires, etc.  The danger is usually from contact of the touch type.  A transferred potential problem generally occurs when a person standing at a remote location away from the substation area touches a conductor connected to the substation grounding grid.  The importance of the problem results from the very high magnitude of potential difference which is often possible.  This potential difference may equal or exceed (due to induced voltage on unshielded communication circuits, pipes, etc.) the grid potential rise (GPR) of the substation during a fault condition.  The basic shock situation for transferred potential is shown in figure 8-1.

An investigation into possible transferred potential hazards is essential in the design of a safe substation grounding network.  Various means can be taken to protect against the danger of transferred potentials.  A brief discussion of the various transferred potential hazards and means to eliminate the hazard follows.

17.9.1  Communication circuits

For communications circuits, schemes have been developed involving protective devices and insulating and neutralizing transformers to safeguard personnel and communications terminal equipment.  These will not be discussed here except to emphasize the importance of adequate insulation and isolation from accidental contact of any of these devices and their wiring which may reach a high voltage with respect to local ground.  The introduction of fiber optics to isolate the substation communications terminal from the remote terminal can eliminate the transfer of high potentials.  Fiber optics should be considered when potentials cannot be easily controlled by more conventional means.

17.9.2  Rails

Rails entering the substation can create a hazard at a remote point by transferring all or a portion of the GPR from the substation to a remote point during a ground fault.  Similarly, if grounded remotely, a hazard can be introduced into the substation area by transferring remote earth potential to within the substation.  These hazards can be eliminated by removing the track sections into the substation after initial use, or by using removable track sections where the rails leave the ground grid area.  However, insulating flanges, as discussed in the following paragraphs, should also be utilitized to provide as much protection as possible when the railroad track is intact for use.

Insulating splices or flanges are manufactured by a variety of vendors.  The general practice is to install two or three sets of these devices such that a rail car would not shunt a single set.  Investigation of these insulating splices has shown that they are primarily designed for electrical isolation of one track from another for signal scheme purposes.  The typical insulated joint consists of a section of track made from an insulated material called an end post, installed between rail ends.  The side members bolting the joint are also insulated from the rail sections.  The breakdown voltage of the insulating joints should be considered in each application.  The insulating joints must be capable of withstanding the potential difference between remote earth and the potential transferred to the joint.

It should be noted, however, that insulating flanges are not recommeded as the primary means of protection, as they may create their own hazardous situations. [B???]  (D. L. Garrett and K .A. Wallace, “A Critical Analysis of Grounding Practices for Railroad Tracks in Electric Utility substations,”  IEEE Transactions on Power Delivery, Vol. 8, No. 1, pp. 90-96, Jan. 1993)  If the track sections outside the substation and beyond the insulating flange are in contact with the soil, a hazardous voltage may exist between that rail section and a rail section or perimeter fence grounded to the substation grid during a fault.  If the rails are not bonded to the substation grid, a hazardous voltage may exist between the rails and grounded structures within the substation during a fault.  Other situations are discussed in [B??? same as above] that may result in hazardous voltages.  Thus, removal of the rails sections at the perimeter of the grounding system is recommended.

17.9.3  Low-voltage neutral wires

Hazards are possible where low voltage feeders or secondary circuits, serving points outside the substation area, have their neutrals connected to the substation ground.  When the potential of the substation ground grid rises as the result of ground-fault current flow, all or a large part of this potential rise may then appear at remote points as a dangerous voltage between this "grounded" neutral wire and the adjacent earth; moreover, where other connections to earth are also provided, the flow of fault current through these may, under unfavorable conditions, create gradient hazards at points remote from the substation.

To avoid these difficulties, the low voltage neutral may be isolated from ground at the substation itself; always provided, however, that this does not result in slowing down the clearing time for low voltage faults to the point where the total hazard is increased rather than diminished.  If the low-voltage neutral is isolated from that substation ground, it then becomes necessary to avoid hazards at the substation due to the introduction, via the neutral wire, of remote earth potential.  This implies that this neutral, in and near the substation, should be treated as a "live" conductor.  It should be insulated from the substation ground system by insulation adequate to withstand the maximum ground-grid potential rise; and it should be located so as to minimize the danger of being contacted by personnel.

17.9.4  Portable equipment and tools supplied from substation

Similar hazards need to be considered in the case of portable mining, excavating, or material handling equipment, or portable tools, which are supplied electrically from the substation and are used outside of the area of the grid where the mesh potential is held within safe limits.  Such loads are often supplied by temporary pole lines or long portable cables.  An example is often seen when an addition to an existing substation is being constructed.

A hazardous transferred potential might appear between equipment and the nearby earth during a fault, if the neutral or grounding wire to the equipment is also connected to the substation ground.  In cases such as these, it is common to isolate the supply circuits from the substation ground; to ground the neutrals and equipment to earth at the site of the work; and to make sure that the maximum fault current to the local ground is limited to a low value that will not itself cause gradient hazards.

17.9.5  Piping

Pipelines and metallic conduit should always be connected to the substation grounding system to avoid hazards within the substation area.  Transferred potentials may be reduced or stopped at the substation boundary by inserting insulating sections of sufficient length to avoid shunting by the adjacent soil.  The insulating sections must be capable of withstanding the potential difference between remote earth and the substation.

17.9.6  Auxiliary buildings

Auxiliary buildings can be treated as part of the substation for grounding purposes, or as separate installations, depending on circumstances.  If the buildings and substation are relatively close, and especially if the buildings are linked directly to the substation by such things as water pipes, cable sheaths, phone lines, etc., it is appropriate to treat such buildings and their immediate area as part of the substation.  As such, the buildings should be grounded using the same safety criteria as the substation.  If the buildings are not as close, and if such conducting links are lacking, it may be decided to treat such buildings as separate units with their own local safety grounds.  If served electrically from the substation, they should have their own distribution transformers of a type to provide adequate insulation against transfer of the substation ground-grid potential rise.  Secondary neutrals would, in this case, be connected to the local ground at the auxiliary buildings only.

17.9.7  Fences

Substation fences have been extended to other areas of a site at some locations.  This also presents a possible transferred potential hazard if the fence is connected to the substation grounding grid.

In order to lessen this hazard, the substation fence should be insulated from the fence leaving the substation area.  It is recommended that two insulating joints be installed in order to prevent someone from bridging one insulating joint by touching the grounded substation fence and the insulated fence, as shown in figure 17-14.

An example of the potential profile of a fence connected to a substation grounding grid and leaving the substation area is shown in figure 17-15.  As can be seen, the touch potential on the fence after it leaves the substation grid area of influence is not safe to contact.

18.  Notes on the construction of a grounding system

Following the ground‑grid design, the grounding plan is usually drawn on the fence and foundation plan drawing.  The ground grid is then ready for construction.

The method, or  combination of methods chosen, will depend on a number of factors, such as size of a grid, type of soil, size of conductor, depth of burial, availability of equipment, cost of labor, and any physical or safety restrictions due to nearby existing structures or energized equipment.

There are two commonly employed methods to install the ground grid.  These are: (1) the trench method and (2) the cable plowing method.  Both of these methods employ machines.  Where these machines are not employed due to lack of space to move them or small size of the job site, the ground grid is installed by hand digging.

18.1  Ground grid construction - trench method

The flags are staked on the perimeter along two sides to identify the spacing between parallel conductors.  These markers also serve as a guide for the trenching machine.  The trenches are dug using a trenching machine usually along the side having the larger number of parallel conductors.  These trenches are dug to the specified depth (usually about 0.5 m or 1.5 ft).  Conductors are installed in these ditches and ground rods are driven and connected to the conductors.  Pigtails for equipment grounds may also be placed at this time.  These initial ditches are then backfilled with dirt up to the location of the cross connections.

The next step is to dig cross conductor ditches (often to a shallower depth), once again using markers as a guide.  Care must be taken when digging these ditches to avoid snagging the conductor laid in the backfilled ditches at cross points.  The conductors are installed in the ditches and any remaining ground rods are driven and connected to the conductors.  Remaining pigtails are also connected to these conductors.  Cross type connections are made between perpendicular conductor runs.  The ditches are then backfilled with dirt.

An alternative method consists of confining the work to a small section of the total yard and completing this section entirely before moving on to a new area.  In this event, the trenches are all dug at the same depth prior to any conductor being placed. Installation of conductors and ground rods are the same as in the previous method.

18.2  Groundgrid construction - conductor plowing method

Another procedure for the installation of ground conductors, which may prove economical and quick when conditions are favorable and proper equipment is available, is to plow the conductors in.  A special narrow plow is used, which may be either attached to, or drawn by, a tractor or four‑wheel drive truck, if there is sufficient maneuver​ing room. The plow may also be drawn by a winch placed at the edge of the yard.  The conductor may be laid on the ground in front of the plow, or a reel of conduc​tor may be mounted on the tractor or truck, or on a sled pulled ahead of the plow.  The conductor is then fed into the ground along the blade of the plow to the bottom of the cut.  Another method is to attach the end of the conductor to the bottom of the plow blade, and pull it along the bottom of the cut as the plow progresses.  In this case, care should be taken to ensure that the conductor does not work its way upward through the loosened soil.

The cross conductors are plowed in at slightly less depth to avoid damage to previously laid conductors.  The points of crossing, or points where ground rods are to be installed, are then uncovered, and connections are made as described in 18.3.

With adequate equipment, and the absence of heavy rock, this method is suitable for all of the conductor sizes and burial depths normally used.  The reader is referred to IEEE Std 590‑1977 (Reaff. 1991) [B???  should this be in references??] for discussion on the subject.

18.3  Installation of connections, pigtails, and ground rods

Once the conductors are placed in their trenches, the required connections are then made.  Generally, the points of crossing require a cross type connection, while tee connections are used for taps to a straight conductor run located along the perimeter.  Types of connections are many and varied and of course depend upon the joint, material being joined, and the standard practice of the utility concerned.  Mechanical.joints utilizing a clamping force or a wedge action as well as brazed or exothermic joints have all been used, as discussed in clause 9.

Exothermic connections utilize a method of welding copper to copper or copper to steel in which an outside source of heat or power is not required.  Powdered metals (copper oxide and aluminum) are poured from a container into a graphite crucible and ignited by means of a flint igniter.  The reduction of the copper oxide by the aluminum (exothermic reaction) produces molten copper and aluminum slag.  The molten copper flows over the conductors in the confines of the graphite mold, melting them and welding them together.

Mechanical joints rely on physical forces to provide adequate pressure to ensure an electrically sound connection.  The necessary force is achievable through the use of hydraulics or mechanics for compression type e fittings, impact or screw action for wedge type fittings, or mechanically tightened bolts and nuts for clamp type bolted fittings.  Some mechanical joint fittings are designed to incorporate a force limiting feature during the installation procedure so as to provide the correct force necessary. These limiting features are of course peculiar to tile par​ticular connector used, but include such items as shear bolts designed to limit torque and precision dies to limit compression.

Pigtails are left at appropriate locations for grounding connections to struc​tures or equipment.  These pigtails may be the same cable size as the underground grid or a different size depending on the number of grounds per device, the magnitude of the ground fault current, and the design practices of the utility concerned.  The pigtails are then readily accessible after backfilling for the grade connections.  The above grade connections are made by the usual methods previously mentioned.

Also prior to backfilling, the installation of the ground rods is usually accomplished.  This may be done using a hydraulic hammer, air hammer, or other mechanical device.  Considerable developmental work has been done in this area and presently an air hammer installed on a truck complete with a ground rod guiding device is available for efficient and easy ground rod driving.

Joining of two ground rods is done either by welding or by using a threaded or threadless coupler. The connection between the ground rod and grid conductor can be made using any method described previously in this clause.

18.4  Construction sequence consideration for ground grid installation

A ground grid is normally installed after the yard is graded, foundations are poured and deeper underground pipes and conduits are installed and backfilled.  The security fence may be installed before or after the ground‑grid installation.  In cases where deeper underground pipes and conduits are not installed before ground grid installation, an attempt should be made to coordinate the trenching procedure in a logical manner.

18.5  Safety considerations during subsequent excavations

As shown previously the insulating value of a layer of clean surface material or gravel is an aid to safety under ground fault conditions.  Therefore, when an excavation is necessary after a rock surfacing has been applied, care should be taken to avoid mixing the lower resistivity soil from the excavation with the surrounding rock surfacing material.

During subsequent excavations there are more chances to snag the ground conductor.  In such a case a check should be made to determine if there is a break in the conductor and joints.  A break in the conductor or joints, or both, must be immediately repaired.  A temporary jumper should be placed around the break before it is repaired.  The jumper should be suitable for the application and installed according to live-line work practices, because a voltage may exist between the two ground conductor ends. 
19.  Field measurements of a constructed grounding system
19.1  Measurements of grounding system impedance

As has already been indicated, only approximate results can usually be expected from a precalculation of substation ground impedance.  A careful measurement of the impedance of the installation as constructed is therefore desirable, though not always practical if the grid is connected to or influenced by other buried metallic structures.

In this clause only general methods are discussed.  For more detailed information refer to ANSI/IEEE Std 81‑1983.  Several important points of this guide have been used here, where applicable.  While in this clause the ohmic value is referred to as resistance, it should be remembered that there is a reactive component that should be taken into consideration when the ohmic value of the ground under test is less than 0.5 .
, and the area is relatively large.  This reactive component has little effect on grounds with an impedance higher than 1 
19.1.1  Two‑point method (ammeter‑voltage method)

This method measures the total resistance of the unknown and an auxiliary ground.  Because the resistance of the auxiliary ground is presumed to be negligible in comparison with the resistance of the unknown ground, the measured value in ohms is then expressed as the resistance of the unknown ground.

This method is subject to large errors for a low value of the unknown ground resistance or when grounds are close to each other, but it may be useful if a "go or no go" type of test is all that is needed.

19.1.2  Three‑point method.  This method involves the use of two test electrodes with their resistances designated as r2 and r3  and with the electrode to be measured designated as r1.  The resistance between each pair of electrodes is measured and designated as r12, r13, and r23, where r12 = r1 + r2, etc.  Solving the simultaneous equations, it follows that:





(83)

Therefore, by measuring the resistance of each pair of ground electrodes in series and substituting these values in equation (83), the value of r1 can be determined.

If the two test electrodes have substantially higher resistances than the elec​trode under test, the errors on the individual measurements will be greatly magnified in the final results.  In addition, this method can give erroneous values, such as zero or negative resistance, if the electrodes are not separated by a sufficiently large distance.  Consequently, when measuring a single driven rod, the spac​ing between the three ground electrodes should be 10 m or more.  For larger areas the minimum spacing should be on the order of the dimensions of the ground system. Consequently, this method then becomes awkward for  large sub​stations.

19.1.3  Ratio method

This method compares the resistance of the electrode under test to that of a known resistance, generally by the same electrode configuration as in the fall‑of‑potential method described in 19.1.3. Being a comparison method, the ohmic readings are independent of the test current magnitude provided that the test current is high enough to give adequate sensitivity.

19.1.4  Staged‑fault tests

It may be necessary to stage a high‑current test where specific information is desired for a particular grounding design.  This test would also give quantities from which the ground impedance could readily be determined.

This type of test would require the use of an oscillograph that would record the voltage between selected points.  However, the magnitude of the voltage may be quite large and require a potential transformer to step down the voltage to a manageable level.  The maximum voltage and potential transformer ratio should be determined in advance of the staged‑fault test so that no test equipment is overstressed.  The fall‑of‑potential test can be used to determine the expected voltage of a staged‑fault test.

Another important consideration is the calibration of the oscillograph circuit, which is composed of a potential transformer with a possible high resistance in the primary.  This resistance is composed of the remote potential ground in series with a long lead.  A satisfactory calibration of the deflection of the oscillograph element may be made by inserting a measured voltage in the primary circuit in series with the lead and the remote potential ground as used during the test.

The location of the actual points to be measured is, of course, dependent on the information desired; but in all cases due allowance should be made for coupling between test circuits.

19.1.5  Fall‑of‑potential method

This method has several variations and is applicable to all types of ground impedance measurements (see figure 19-1).  Basically, the ground resistance measurement consists of measuring the resistance of a body of earth surrounding the grounding system. Thus, only one end of the resistance is definitely available, the grounding system itself. The other end is not practically available and is called  the “remote electrode” or “remote soil.”  The remote electrode is theoretically at an infinite distance from the grounding system where the earth current density approaches zero.  Although the fall-of-potential method is universally used, it presents may difficulties and sources of error when used to measure the resistance of large grounding systems usually encountered in practice.  These difficulties occur mainly because of the size and configuration of the grounding system and soil heterogeneity.

If the distance D is large enough with respect to the grounding system the center part of the fall-of-potential curves tend to be nearly horizontal but it may appear to do so also because of lack of sensitivity of the instruments used.  It is usually accepted, although not correctly, that the nearly horizontal section of the curve gives the true resistance Re.  For large grounding systems, large distances D may not be practical or even possible and as a result, the nearly horizontal section of the curve will not exist.  In this case accurate measurements will not be obtained unless one has already a good idea of the exact probe position P.

For measuring resistance, the current source is connected between the substation ground mat E and a current electrode located at a distance of several hundred meters from the substation.  The potential‑measuring circuit is then connected between the substation mat E and a potential electrode P, with measurements being made at various locations of the electrode outside the substation.  This potential electrode may be moved toward the current electrode in equal increments of distance, starting near the substation, and the resistance readings obtained at the various locations may be plotted against distance from the substation.  The resulting graph should resemble curve EPC of Figure 19-1(b).  From E to P, the voltage per ampere of test current rises, but the voltage gradient decreases reaching a minimum at P. Continuing toward C, the effect of current converging on the current test probe becomes apparent and a rising voltage gradient is observed as the current probe is approached.  The slowly rising, nearly horizontal portion of the graph represents a zone where the effect of current convergence toward the ends of the current circuit is negligible. When the return electrode is placed at a finite distance from the grounding system and the potential probe is driven at a specific location, then an accurate measurement of the resistance is obtained.  Unfortunately, the exact location of the potential electrode is well defined only for some ideal cases such as hemispherical or very small electrodes buried in uniform or two layer soils. [B??]  The case of a large grounding system buried in uniform soil assuming uniform current density distribution in the conductors has been analyzed by Curdt [B??] and Tagg [B??].  In practice, however, grounding systems consist of a complex arrangement of vertical ground rods and horizontal conductors, usually buried in non uniform soils.

Figure 19-1 {old fig 27}

Figure 27
(a)Fall‑of‑potential method and
(b) Earth surface potentials for various spacings "X"
For large grounding grids the spacings required may not be practical or even possible, especially where the transmission line overhead ground wires and feeder neutrals connected to substation ground effectively extend the area of influence. Consequently, the so called flat portion of the curve will not be obtained and other methods of interpretation must be used.  Note also that previous work has shown that when soil is not uniform and separation is not large compared to ground system dimensions the 61.8 percent rule which corresponds to the so called flat portion of the curve may no longer apply [B??] [B??].  Locations varying from 10 percent to 90 percent were found to be quite possible.  These methods are discussed in IEEE Std 81‑1983.

It should be noted that placement of the potential probe P at the opposite side with respect to electrode C (that is, at P2) will always result in a measured apparent impedance smaller than the true resistance.  In addition, when P is located on the same side as electrode C (that is, at P1), there is a particular location that gives the true resistance.

The primary advantage of the fall‑of‑potential method is that the potential and current electrodes may have substantially higher resistance than the ground system being tested without significantly affecting the accuracy of the measurements.

20.  Physical scale models
It often is difficult to draw valid conclusions concerning a general grounding problem solely from actual field data.  The lack of consistent results caused by the inability to control the test, such as weather conditions, and other variables affecting the condition of the sod, and difficulties in data collecting, all hamper the ability to run and duplicate tests.  Because it is helpful to have verification of theoretical assumptions or computer techniques, or both, scale models have been used to bridge the gap.  Models can be used to determine the resistance and potential profiles of ground‑grid arrangements.

The early scale model tests used water to represent uniform soil.  Using small models in large tanks gave consistent results and enabled various models and conditions to be tested and the effects of different parameters to be observed.

In the late 1960's, a two‑layer laboratory model was developed at Ecole Polytechnique to verify computer techniques .[B101]  This method used concrete blocks to represent the lower layer of soil.  A technique was later developed by Ohio State University that used agar, a gelatin‑like substance frequently used in biological studies, to simulate the lower levels of soil.  EPRI Project 1494‑3 [B127] describes the methodology for performing such model tests.  In this project, accurate uniform soil and two‑layer soil models were used to study the effects of many parameters on resistance and surface potentials.

The results of model tests have shown that scale models can be effectively used for parametric studies for grounding grid design and for verifying computer simulations of ground‑grid parameters. [B133]

Annex  A

Bibliography

(Informative)

[B1] AIEE Working Group on Substation Grounding Practices.  Application Guide on Methods of Substation Grounding.  AIEE Transactions, vol 73, part 111‑A, 1954, pp 271‑278.

[B2] Analysis Techniques for Power Substation Grounding Systems EPRI Final Report El,‑2682, vols 1 and 2, Oct 1982.

[B3] Armstrong, H. R., Grounding Electrode Characteristics from Model Tests. AIEE Transactions, vol 72, part III, 1953, pp 1301 ‑ 1306.

[B4] Armstrong, H.R., and Simpkin, L. J., Grounding Electrode Potential Gra​dients from Model Tests.  IEEE Transactions on Power Apparatus and Systems, Oct 1960, pp 618-623.     Not found in guide.
[B5] Barbeito, N., Substation ground Grid Tests: Presented at the Southeastern Electric Exchange, June 1-3, 1988

[B6] Barbeito, N., “Substation Ground Grid Tests”, Southeastern Electric Exchange Conference, June 2, 1988.
[B7] Bellaschi, P. L., Lightning Currents in Field and Laboratory.  AIEE Transactions, vol 54, 1935, pp 837‑843.

[B8] Biddle, James, G., Company, Getting Down to Earth, Manual on Earth Resistance Testing (25T), 1970

[B9] Biegelmeier, U. G., Die Bedeatung der Z‑Schwelle des Herzkammerfilim​merns fur die Festlegung von Beruhrunggsspanungs greuzeu bei den Schutzma Bradhmer gegen elektrische Unfate.  E&M, vol 93, no 1, 1976, pp 1‑8.

[B10] Biegelmeier, U. G., and Rotter, K., Elektrische Widerstrande und Strome in Merischlicken Korper.  E&M, vol 89, 1971, pp 104‑109.

[B11] Biegelmeier, U. G., and Lee, W. R., New Considerations on the Threshold ot Ventricular Fibrillation for AC Shocks at 50 ‑ 60 Hz, Proceedings of the IEEE, vol 127, 1980, pp 103 ‑110.

[B12] Blattner, C. J., Study of Driven Ground Rods and Four Point Soil Resistivity Tests, IEEE Transactions on Power Apparatus and Systems, vol PAS‑101, no 8, Aug 1982, pp 2837‑2850.  Not found in guide.
[B13] Blattner, C. J., “Analysis of Soil Resistivity Test Methods in Tow-Layer Earth, IEEE Transactions, Vol., 104, No. 12, December 1985

[B14] Blattner, C.J., and Dawalibit, F., “Earth Resistivity Measurement Interpretation Techniques”, IEEE Transactions, Vol., 103, No. 2, February, 1984

[B15] Blattner, C. J., “Prediction of Soil Resistivity and Ground Rod Resistance for Deep Ground Electrodes”, IEEE Transactions, Vol. 99, No. 5, September/October, 1980

[B16]  Blattner, C. J., “Study of Driven Ground Rods and Four Point Soil Resistivity Data, IEEE Transactions, Vol. PAS 101, No. 8, pp 2837-2850, August, 1982

[B17] Bodier, M. G., La Secrites des Personnes et la Question des Mises a la Terre dans les Postes de Distribution, Bulletin de la Societe' Francaise des Electriciens, ser 6th, vol VII, no 74, Oct 1947, pp 545-562.

[B18] Bodier, M. G., Systematic Investigation of Potential Gradients In and Around a Transformation Substation.  Bulletin de la Societe' Francaise des Electriciens, July 1951.

[B19] Bogajewski, W., Dawalibi, F., Gervais, Y., and Mukhedkar, D., Effects of Sustained Ground Fault Current on Concrete Poles.  Paper 81 WM 202‑1, presented at the IEEE‑PES Winter Meeting, Atlanta, GA, Feb 1981.

[B20] Carson, J. R., Wave Propagation in Overhead Wires with Ground Return. Bell Systems Technical Journal, vol 5, 1926.

[B21] Clem, J. E., Reactance of Transmission Lines With Ground Return.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑50, Sept 1931, pp 901 ​918.

[B22] Computation of Zero Sequence Impedances of Power Lines and Cables.   Engineering Report no 37, Joint Subcommittee on Development and Research of EEI and Bell Telephone Systems, July 22, 1936.

[B23] Conversion Subcommittee of AIEE Substations Committee.  Recommended Grounding Practices for Single Polarity DC Structures.  Paper no 57‑719, AIEE Transactions, vol 76, part III, 1957.

[B24] Crawford, E., and Griffith, M., A Closer Look at "The Facts of Life" in Ground Mat Design.  IEEE Transactions an Industry Applications, vol IA‑ 15, no 3, May/June 1979, pp 241‑250.

[B25] Currents in Earth Wires at the Top of Pylons and  Their Effect on the Poten​tials of the Pylons and Stations in the Neighborhood of a Point of Short‑Circuit to Earth. Contribution no 78, CCITT, Study Group V, Nov 1963.

[B26] Dalziel, C. F., A Study of the Hazards of Impulse Currents.  AIEE Trans​actions, vol 72, part III, Oct 1953, pp 1032‑1043.

[B27] Dalziel, C. F., Dangerous Electric Currents.  AIEE Transactions, vol 65, 1946, pp 579‑585, 1123-1124.

[B28] Dalziel, C. F., Effect of Wave Form on Let‑Go Currents.  AIEE Transactions, vol 62, 1943, pp 739‑744.

[B29] Dalziel, C. F., Electric Shock Hazard.  IEEE Spectrum, Feb 1972, pp 41‑50.

[B30] Dalziel, C. F., Threshold 60‑Cycle Fibrillating Currents. AIEE Transactions, vol 79, part III, 1960, pp 667‑673.   Not found in guide.
[B31] Dalziel, C. F., and Lee, R. W., Reevaluation of Lethal Electric Currents. IEEE Transactions on Industry and General Applications, vol IGA‑4, no 5, Oct 1968, pp 467‑476.

[B32] Dalziel, C. F., Temporary Paralysis Following Freezing to a Wire.  AIEE Transactions, vol 79, part III, 1960, pp 174‑175.

[B33] Dalziel, C. F., Lagen, J. B., and Thurston, J. L., Electric Shock.  AIEE Transcations, vol 60, 1941, pp 1073‑1079.

[B34] Dalziel, C. F., and Lee, W. R., Lethal Electric Currents.  IEEE Spectrum, Feb 1969, pp 44‑50.

[B35] Dalziel, C. F. and Mansfield, T. H., Effect of Frequency on Perception Currents. AIEE Transactions, vol 69, 1950, pp 1161 1168.

[B36] Dalziel, C.F., and Massogilia, F.P., Let-Go Currents and Voltages. AIEEE Transactions, vol 75, part II, 1956, pp 49‑56.

[B37] Dalziel, C.F., Ogden, E., and Abbott, C.E., Effect of Frequency on Let-Go Currents, AIEE Transactions, vol 62, Dec 1943, pp 745-750 and 1000.

[B38] Dawalibi, F., and Mukehedkar, D., Ground Fault Current Distribution in Power Systems--The Necessary Link. Paper A77 754-5, presented at the IEEE Summer Power Meeting, Mexico City, 1977.    Not found in guide.
[B39] Dawalibi, F., Ground Fault Current Distribution Between Soil and Neutral Conductors.  IEEE Transactions on Power Apparatus and Systems, vol PAS-99, no 2, Mar/Apr 1980, pp 452-461.

[B40] Dawalibi, F., Boucimd, M., and Mukhedkar, D., Survey on Power System Grounding Design Practices.  IEEE Transactiorns on Power Apparatus and vol PAS‑99, no 4, July/Aug 1980, pp 1396‑1405.

[B41] Dawalibi, F., and Mukhedkar, D., Influence of Ground Rods on Ground​ing Systems. IEEE Transactions on Power Apparatus and Systems, vol PAS‑98, no 6, Nov/ Dec 1979, pp 2089‑2098.    Not found in guide.
[B42] Dawalibi, F., and Mukhedkar, D. Optimum Design of Substation Ground​ing in Two‑Layer Earth Structure; Part I ‑ Analytical Study, Part 11 ‑ Compari​son Between Theoretical and Experimental Results, and Part Ill ‑ Study of grounding grids Performance and New Electrodes Configuration.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑94, no 2, Mar/Apr 1975, pp 252-261, 262-266, 267-272.

[B43] Dawalibi, F., and Mukhedkar, D., Parametric Analysis of Grounding Systems. IEEE Transactions on Power Apparatus and Systems, vol PAS‑98, no 5, Sept/Oct, 1979, pp 1659‑1668.

[B44] Dawalibi, F., Mukhedkar, D., and Bensted, D., Soil Effects on Ground Fault Currents.  IEEE Transactions on Power Apparatus and Systems, vol PAS​100, July 1982, p 3442.

[B45] Dawalibi, F. P., Southey, R. D, and Baishiki, R. S. "Validity of Conventional Approaches for Calculating Body Currents Resulting From Electric Shocks". IEEE Transactions on Power Delivery, Vol.5, pp 613-626. 1990

[B46]  Dawalibi, F. P., Xiong, W., and Ma, J. "Effects of Deteriorated and Contaminated Substation Surface Covering Layers on Foot Resistance Calculations". IEEE Transactions on Power Delivery, Vol.8, pp 104-113, 1993

[B47]  Dawalibi, F. P., and Ma, J., and Southey, R. D., “Behavior of Grounding Systems in Multilayer Soilers: A Parametric Analysis” IEEE/PES Winter Power Meeting, Paper 93 EM 12202 PWRD, 1993

[B48] Dawalibi, F., and Barbeito, N., “Measurements and Computations of the Performance of Grounding Systems Buried inMultilayer Soils”, IEEE Transactions, Vol. 6, No. 4 pp 1483-1490, October 1992

[B49] Deri, A., Tevan, G., Semlyen, A., and Castanheira, A., The Complex Ground Return Plane ‑ A Simplified Model for Homogeneous and Multilayer Earth Return.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑100, no 8, Aug 1981, pp 3686‑3693.

[B50] Desieno, C. F., Marchenko, P.P., and Nassell, G.S., General Equations for Fault Currents in Transmission Line Ground Wires.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑89, Nov/Dec 1970, pp 1891‑1900.

[B51] Dick, E. P., Fujinmoto, N., Ford, G. L., and Harvey, S., Transient Ground Potential Rise in Gas‑Insulated Substations ‑ Problem Identification and Mitigation. IEEE Transactions on Power Apparatus and Systems, vol PAS 101, no 10, Oct 1982, pp 3610-3619.

[B52] Dick, W. K., and Holliday, H. R., Impulse and Alternating Current Tests on Grounding Electrodes in Soil Environment.  IEEE Transactions on Power Apparatus and Systems, vol PAS-97, no 1, Jan/Feb 1978, pp 102‑108.

[B53] Dodds, T. H., and Spindle, H. E., Grounding of Gas Insulated Substations. IEEE Transactions on Power Apparatus and Systems, vol PAS‑94, no 4, July/Aug 1975, pp 1183‑1191.

[B54] Elek, A., Hazards of Electric Shock at Stations During Fault and Method of Reduction.  Ontario Hydro Research News, vol 10, no 1, 1958, pp 1‑6.

[B55] Endrenyi, J., Fault Current Analysis for Substation Grounding Design. Ontario Hydro Research Quarterly, 2nd Quarter, 1967.

[B56] Endrenyi, J., Analysis of Transmission Tower Potentials During Ground Faults. IEEE Transactions on Power Apparatus and Systems, vol PAS‑86, Oct 1967, pp 1274‑1283.

[B57]  Endrenyi, J., “Evaluation of Resistivity Test for Design of Station Grounds in Non-Uniform Soil”, IEEE Transactions on PAS, Vol. 84, pp 996-970, December, 1963

[B58] EPRI Transmission Line Reference Book 345 kV and Above.  Electric Power Research Council, Palo Alto, CA, 1975.

[B59]  EPRI EL2683, Analysis Techniques for Power Substation Grounding Systems, Georgia Institute of Technology, July, 1992

[B60]  EPRI EL-3982, Soil Resistivity Tests Using Modeling Techniques Ohio State University, May, 1985

[B61]  EPRI EL-2699  Transmission Line Grounding; Safe Engineering Services, Chapter 4, (Resistivity) and Chapter 9 (Field Measurement Techniqes), October, 1982

[B62]  EPRI TR-100863, Seasonal Varations of Grounding Parameters by Field Tests,  July, 1992

[B63] Ewy, K. A., and Smolleck, H. A., A Graphical Explanation of the Resist​ance and Surface‑Potential Calculations for Grounding Systems in Two‑Layer Earth.  Paper 83 SM 430‑6, presented at the 1983 IEEE‑PES Summer Power Meet​ing, Los Angeles, CA.    Not found in guide.
[B64] Fagan, E. J., and Lee, R. H., The Use of Concrete‑Enclosed Reinforcing Rods as Grounding Electrodes.  IEEE Transactions on Industry and General Applications, vol IGA‑6, no 4, July/Aug 1970, pp 337‑348.

[B65] Ferris, L. P., King, B. G., Spence, P. W., and Williams, H., Effect of Elec​tric Shock on the Heart.  AIEE Transactions, vol 55, May 1936, pp 498 ‑ 515, 1263.

[B66] Ford, G. L., and Geddes, L. A., Transient Ground Potential Rise in Gas​Insulated Substations ‑ Assessment of Shock Hazard.  IEEE Transactians on Apparatus and Systems, vol PAS‑101, no 10, Oct 1982, pp 3620‑3629.

[B67]  Gagnon, J., and Mukhedkar, D., “Earth Resistivity Measurement in a Two-Layer Structure”, IEEE Transactions, Vol. PAS-93, 1974 (We need a copy of this paper)
[B68] Garrett, D. L., Determination of Maximum Ground Fault Current Through Substation Grounding System Considering Effects of Static Wires and Feeder Neutrals, Proceedings of Southeastern Electric Exchange, Atlanta, GA, 1981.

[B69] Garrett, D. L. and Holley, H. J., Calculation of Substation Ground Resistance Using Matrix Techniques.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑99, no 5, Sept/ Oct 1980, pp 2008 ‑ 2011.

[B70] Geddes, L. A., and Baker, L. E., Response to Passage ot Electric Current Through the Body.  Journal of Association for the Advancement of Medical Instruments, vol 2, Feb 1971, pp 13-18.

[B71] Gieiges, K. S., Electric Shock Hazard Analysis.  AIEE Transactions, vol 75, part III, 1956, pp 1329‑1331.

[B72] Graybill, H. W., Koehler, H. C., Nadkarni, J. D., and Nicholas, J. H., Termination of High‑Pressure Oil Cables in Gas‑Insulated Minisubstation Equipment.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑93, no 5, Sept/Oct 1974, pp 1669‑1674.

[B73] Gross, E. T. B., et al.  Grounding Grids for High Voltage Stations.  AIEE Transactions, vol 72, Aug 1953, pp 799‑810.  Not found in guide. 

[B74] Heppe, R. J., Computation of Potential at Surface Above an Energized Grid or Other Electrode, Allowing for Nonuniform Current Distribution.  IEEE Trans​actions on Power Apparatus and Systems, vol PAS‑98, no 6, Nov/Dec 1979, pp 1978 ‑ 1989.

[B75] Heppe, R. J., Step Potentials and Body Currents for Near Grounds in Two​ Layer Earth.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑98, no 1, Jan / Feb 1979, pp 45 ‑ 59.   Not found in guide.
[B76] IEEE Working Group on Electrostatic Effects of Transmission Lines, Gen​eral Systems Subcommittee.  Electrostatic Effects of Overhead Transmission Lines, Part I ‑Hazards and Effects, IEEE Transactions on Power Apparatus and Systems, vol PAS‑91, Mar/Apr 1972, pp 422‑426.

[B77]  IEEE Std 80-1986, (Practical Applications), IEEE Tutorial Course Text 86, EH-253-5-PWR, Chapter 2, (Soil Resistivity Analysis)

[B78]  Jackson, J. D., "Classical Electrodynamics," (book), John Wiley & Sons, Inc. 

[B79] Jones, W. R., Bentonite Rods Assure Ground Rod Installation in Problem Soils. IEEE Transactions on Power Apparatus, vol PAS‑99, no 4, July/Aug 1980, pp 1343‑1346.

[B80] Joy, E. B., Meliopoulos, A. P., and Webb, R. P., Touch and Step Calculations for Substation Groundings Systems.  Paper A-79‑052‑2, presented at IEEE/PES Winter Power Meeting, New York, NY, Feb 1979.

[B81] Kercel, S. W., Design of Switchyard Grounding Systems Using Multiple Grids.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑100, no 3, Mar 1981, pp 1341 ‑1350.

[B82] Kinyon, A. L., Earth Resistivity Measurements for Grounding Grids.  AIEE Transactions, vol 20, Dec 1961, pp 795‑800.

[B83] Kiseiev., Research into Electric Shock. Electrical Review, vol 3l, Dec l965.

[B84] Kouwenhoven, W. B., et al.  AC Shocks of Varying Parameters Affecting the Heart. AIEE Transactions, vol 78, part I, 1959, pp 163 ‑ 169.

[B85] Langer, H., Messungen von Erderspannungen in einem 220 kV Umspanwerk. Electrotechnische Zietschrift, vol 75, no 4, Feb 1954, pp 97‑105 (English translation available in AIEE No. 80‑1961, Appendix V, pp 91 102).

[B86]  Lazzara, J., and Barbeit, N., “Simplified Two-layer Model Substation Ground Grid Design Methodology”, IEEE Transactions, Vol., 5, No. 4, pp 1741-1750, November 1990

[B87] Laurent, P. G., Les Bases Generates de la Technique des Mises a la Terre dans les Installations Electriques.  Bulletin de la Societe' Francaisee des Electriciens, vol 1, ser 7, July 1951, pp 368‑402.
[B88]  Laurent, P. G. "Les Bases Generales de la Technique des Mises a la Terre dans les Installations Electriques". Bulletin de la Societe Francaise des Electriciens, Vol.1, Ser.7, pp 368-402, July, 1951

[B89] Lee, W. R., Death from Electrical Shock.  Proceedings of the IEEE, vol 113, no 1, Jan 1966, pp 144‑148.

[B90] Loucks, W. W., A New Approach to Substation Grounding. Electrical News and Engineering, May 15, 1954.

[B91] Mahonar, V. N., and Nagar, R. P., Design of Steel Earthing Grids in India. IEEE Transactions of Power Apparatus and System, vol PAS‑98, no 6, Nov/Dec 1979, pp 2126 ‑2134.

[B92] Manual on Ground Resistence Testing.  Publication no 25‑J, James G. Bid​dle Co, 1952.

[B93] Meliopoulos, A. P., Papalexopoulos, A., and Webb, R. P., Current Division in Substation Grounding System.  Proceedings of the 1982 Protective Relaying Conference, Georgia Institute of Technology, Atlanta, GA, May 1982.

[B94]  Meliopoulos, A. P. S., Xia, F., Joy, E. B., Cokkinides, G. J., "An Advanced Computer Model for Grounding System Analysis". IEEE Transactions on Power Delivery, Vol.8, pp 13-23, 1993

[B95]  Meliopoulos, A.P., Papelexopoulos, A. D., Webb, R., and Blattner, C. J., “Estimation of Soil Parameters from Driven-Rod Measurements”, IEEE Transactions, Vol. 103, No. 9, September, 1994

[B96] Meliopoulos, A.P., and Papelexopoulos, A. D., “Interpretations of Soil Resistivity Measurement Experience with the Model SOMIP” IEEE Transactions, October, 1986

[B97] Miller, HART, and BROWN.,  Stray Current and Galvanic Corrosion of Rein​forced Steel in Concrete.  Material Performance, vol 15, no 5, May 1976, pp 20 ‑ 27.

[B98] Mitani, H., Magnitude and Frequency of Transient Induced Voltage in Low‑Voltage Control Circuits of Power Stations and Substations.  IEEE Transactions on on Power Apparatus and Systems, vol PAS‑99, no 5, Sept/Oct 1980, pp 1871‑ 1878.   Not found in guide.
[B99]  Moore, R., “An Empirical Method of Interpretation of Earth Resistivity Measurements”, Amercian Institute of Mning Engineering, Column, 164, pp 197-231, 1945 (We need a copy of this paper)
[B100] Morgan, V. T., Rating of Conductors for Short‑Design Currents.  Proceed​ings of the IEEE, vol 118, no 3‑4, Mar/Apr 1971, pp 555 ‑ 570.

[B101] Mukhedkar, D., Gervais, Y., and Dejean, J. P., Modeling a Grounding Electrode. IEEE Transactions on Power Apparatus and System, vol PAS‑92, no 1, Jan 1973, pp 295‑297.

[B102] Mutual Design Considerations for Overhead AC Transmission Lines and Gas Transmission Pipelines.  EPRI Final Report EL‑904, vols 1 and 2, Sept 1978.

[B103] Nahman, J. M., and Salamon, D. D., Analytical Expressions for the Resist​ance of Grounding Grids in Nonuniform Soil.  IEEE Transactions on Power Appa​ratus and Systems, vol PAS‑103, pp 880‑885, Apr 1984.

[B104] Nahman, J.M., and Salamon, D.D.,  Analytical Expressions for the Resist​ance of Rodbeds and of Combined Groundinq System in Noununiform Soil.  IEEE Paper 86 WM126‑7, presented at the IEEE‑PES Winter Meeting, New York, Feb 2 ‑ 7, 1986.

[B105]  Nahman, J. M., and Salamon, D., “A Practical Method for the Interpretation of Earth Resistivity Data Obtained from Driven Rod Tests”,  IEEE Transactions, Vol. 3, No. 4, October, 1988

[B106] Nieman, J., Unstellung von Hochstspannungs‑Erdungsalagen Aufden Be​trieb Mit Starr Geerdetem Sternpunkt.  Electrotechnische Zeitschrift, vol 73, no 10, May 1952, pp 333‑337.

[B107] Nunnally, H. N., Webb, R. P., Joy, E. B., and Meliopoulos, A. P., Com​puter Simulation for Determining Step and Touch Potentials Resulting from Faults or Open Neutrals, in URD Cable.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑98, no 3, May/June 1979, pp 1130‑1136.   Not found in guide.
[B108] Ollendorff, F., Erdstrome (Ground Currents).  Stuttgart, Germany: Springer‑Verlag, 1928; Burkhauser‑Verlag‑Baselund, 1969.

[B109]  Orellara, E., and mooney, H. M., “Two and Three Layer Master Curves and Auxiliary Point Diagrams for Bertical Electrical Sounding Using Wenner Arrangement”,  Interciencia, 1972 Madrid-13, Spain

[B110] Osypka, P., Quantitative Investigation of Current Strength and Routing in AC Electrocution Accident Involving Human Beings and Animals.  Technische Hochschule Braunschweig, Brunswick, West Germany, 1966/SLA Translation Center TT-6611470.

[B111] Palmer, L. S., Examples of Geotechnical Surveys.  Proceedings of the IEE, Paper 2791‑M, vol 106, June 1959, pp 231‑244.

[B112] Patel, S. G., Field Measurements at Texas Valley Substation.  Presented at the Workshop on High Voltage Power System Grounding, Georgia Institute of Technology, Atlanta, GA, May 12‑14, 1982.

[B113]  Purdy, A. B., “Accurate Equations for the Characteristics of Rod Eelctrodes in a Homogeneous Medium”, IEEE PES Winter Meeting, 1979

[B114]  Roman, I., “Some Interpretations of Earth Resistivity Data”, American Institute of Mining and Metallurgical Engineering, Vol. 110, pp. 183-200, 1934

[B115] Rosa, E. B., McCollum, B., and Peters, 0. S., Electrolysis in Concrete. Department of Commerce, Technical Paper of Bureau of Standards, no 18, Mar 1913, pp 1 ‑ 137.

[B116] Rudenberg, R., Distribution of Short‑Circuit Currents in Ground.  Elektro​technische Zeitschrift, vol 31, 1921.    Not found in guide.
[B117] Rudenberg, R., Basic Considerations Concerning Systems.  Etectrotech​nische Zeitschrift, vols 11 and 12, 1926.

[B118] Rudenberg, R., Grounding Principles and Practices‑1, Fundamental Con​siderations on Grounding Currents.  Electrical Engineering, vol 64, no 1, Jan 1945, pp 1 - 13.

[B119] "Safe Substation Grounding, Part l," IEEE Conimittee Report, J. G. Sverak, Chairman, IEEE Transactions on Power Apparatus and Systems, vol PAS‑100, no 9, pp 4281‑4290, Sept 1981.
    Not found in guide.
[B120] "Safe Substation Grounding, Part II," IEEE Committee Report, J. G. Sverak, Chariman, IEEE Transactions on Power Apparatus and Systems, vol PAS‑101, no 10, pp 4006‑4023, Oct 1982.26    Not found in guide.
[B122] Schlichter, “The Interpretation of the Resistivity Prospecting Method for Horizontal Structures”, Physics, Vol. 4, pp 307-322, September, 1933

[B122] Schwarz, S. J., Analytical Expression for Resistance of Grounding Sys​tems.  AIEE Transactions,, vol 73, part III‑B, 1954, pp 1011 ‑ 1016.

[B123] Sebo, S. A. Zero Sequence Current Distribution Along Transmission Lines. IEEE Transactions on Power Apparatus and Systems, vol PAS‑88, June 1969, pp 910‑919.

[B124] Semlyen, A., Ground Return Parameters of Transmission Lines as Asymp​totic Analysis tor Very High Frequencies.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑100, no 3, Mar 1981 pp 1031‑ 1038.

[B125] Smith, G. E., Resistivity of Some Surface Coverings Used in Substation Yards as a Function of Resistivity of the Wetting Agent and as a Function of Time After Wetting. Internal Report of Carolina Power and Light Co, Apr 20, 1978.   Not found in guide.
[B126] Stauffacher, E. R., Short Time Current Carrying Capacity of Copper Wire.  General Electric Review, vol 31, no 6, June 1928, pp 326‑327.Not found in guide.
[B127] Substation Grounding Scale Model Tests.  EPRI Interim Report EL‑3099, May 1983.

[B128] Sunde, E. D., Earth Conduction Effects in Transmission Systems.  New York: McMillan, 1968.

[B129] Sunde, E. D., "Earth Conduction Effects in Transmission Systems". (book), Dover Publications, Inc., New York, 1968.

[B130] Sverak, J. G., Optimized Grounding Grid Design Using Variable Spacing Technique. IEEE Transactions on Power Apparatus and Systems, vol PAS‑95, no 1, Jan/Feb 1976, pp 362‑374.   Not found in guide.
[B131] Sverak, J. G., Simplified Analysis of Electrical Gradients Above a Ground Grid; Part I ‑ How Good is the Present IEEE Method? IEEE Transactions on Power Apparatus and Systems, vol PAS‑103, no 1, Jan 1984, pp 7‑25.

[B132] Sverak, J. G., Sizing of Ground Conductors Against Fusing.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑ 100, no 1, Jan 1981, pp 51 ‑ 59.

[B133] Sverak, J. G., Booraem, C. H., and Kasten, D. G., Post‑Design Analysis and Scale Model Tests for a Two Grid Earthing System Serving the 345 kV GIS Facilities at Seabrook Power Plant.  Paper 410‑06, Proceedings of the CIGRE Sym​posium on High Currents in Power Systems Under Normal, Emergency and Fault Conditions, Brussels, , June 3‑5 1985.

[B134] Tagg, G. F., Earth Resistances.  New York: Pitman, 1964.    Not found in guide.
[B135]  Tagg, G. F., Interpretation of Resistivity Measurements”, American Institute of Mining and Metallurgical Engineering Transactions, Vol. 110, pp135-147, 1934

[B136]  Takahashi, T., and Kawase, T., “Analysis of Apparent Tesistivity in Multi-Layer Earth Structure” IEEE Transactions, Vol. 5, No. 2, April, 1990

[B137] Taylor, H. G., The Earth‑Loading Capacity of Earth Electrodes.  IEE Journal, vol 77, Oct 1935, p 542.  Not found in guide.
[B138] Thapar, B., and Gross, E. T. B., Grounding Grids for High Voltage Sta​tions ‑ Part IV‑Resistance of Grounding Grids in Nonuniform Soil.  IEEE Tran​sactions on Power Apparatus and Systems, vol PAS‑82, Oct 1963, pp 782 ‑ 788.

[B139]  Thapar, B., Gerez, V., Singh, V., "Effective Ground Resistance of the Human Feet in High Voltage Switchyards". IEEE Transactions on Power Delivery, Vol.8, pp 7-12, 1993

[B140]  Thapar, B., Gerez, V., Emmanuel, P., "Ground Resistance of the Foot in Substation Yards". IEEE Transactions on Power Delivery, Vol.8, pp 1-6, 1993

[B141]  Thapar, B., Gerez, V., Kejriwal, H., "Reduction Factor for the Ground Resistance of the Foot in Substation Yards". IEEE/PES 1993 Winter Meeting, Paper # 93WM 121-4-PWRD.

[B142] Thapar, B., and Gross, E. T. B., “Grounding Grids for High Voltage Stations”, IEEE Transactions on PAS, October, 1963

[B143] Towne, H. M., Lightning Arrester Grounds ‑ Parts I, II, and III.  General Electric Review, vol 35, Mar ‑ May, 1932, pp 173 ‑ 280.

[B144]  Ufermann, J., and Jahn, K., “High Frequency Earth Resistance Measuring Instrument, Brown and Boverie Journal, No. 3/67, pp 132-135

[B145] Use of Aluminum for Substation Buses.  Working Group 57.1. IEEE Paper 62-280.  Not found in guide.
[B146] Verma, R., Merand, A., and Barbeau, P., Design of Low Resistence Grounding System for Hydro‑Electric Plant Located on Highly Resistive Soils.  IEEE Transactions of Power Apparatus and Systems, vol PAS‑97, no 5, Sept/Oct 1978, pp 1760‑1768.

[B147] Verma, R., and Mukhedkar, D., Ground Fault Current Distribution in Substation, Towers and Ground Wire.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑98, May/,June 1979, pp 724 ‑ 730.

[B148]  Wenner, F., A Method of Measuring Earth Resistances.  Bulletin of the Bureau of Standards, Rep no 258, vol 12, no 3, Feb 1916, pp 469‑482.

[B149] Yu, L., Determination of Induced Currents and Voltages in Earth Wires During Faults.  Proc.  IEE, vol 120, no 6, June 1973, pp 689‑692.  Not found in guide.
[B150] Zaborszky, J., Efficiency of Grounding Grids with Nonuniform Soil. AIEE Transactions, vol 74, Dec 1955, pp 1230 ‑ 1233.  Not found in guide.

Moved from References

ASTM D448-80, Specifications for Standard Sizes of Coarse Aggregate for High Construction (ANSI).

IEEE C37.010-1979, IEEE Application Guide for AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis (ANSI).

Annex  B

Sample calculations

(Informative)

This annex illustrates the application of equations, tables, and graphs for designing a substation grounding system.  The specific objectives are as follows:


(1) To show the application of principal equations of the guide for several refinements of the design concept toward a satisfactory final design solution


(2) To illustrate the typical differences to be expected between results obtained using the simplified calculations of this guide and the more rigorous computer solutions.


(3) To illustrate such design conditions for which the use of simplified calculations of this guide would not be appropriate for a safe design, as some of the equations may only be used with caution.

In view of these objectives, the following series of examples B1‑B5 neither represents, nor is intended to be, the best or most efficient way to design a grounding system.

The SGA package of computer-based grounding programs, described in EPRI's Final Report EL ‑ 2682, Vol. 2, was used to model the grids in these examples.[B??   ]  This is not intended as an endorsement, and there is no claim made as to the accuracy or validity of these programs.

For the series of examples B1‑B3, the design data are as follows:


Fault duration tf
= 0.5 s


Fault impedance Z1
= 4.0 + j10.0 (

Fault impedance Z0
= 10.0 + j40.0 (

Current division factor Sf
= 0.6


Line‑to‑line voltage at worst‑fault location
= 115,000 V


Soil resistivity (
= 400 (‑m


Crushed rock resistivity (wet) (s
= 2500 (‑m


Thickness of crushed rock surfacing hs
= 0.1 m (4 in)


Depth of grid burial h
= 0.5 m


Available grounding area A
= 63 m ( 84 m

The crushed rock resistivity is assumed to be a conservative estimate based on actual measurements of typical rock samples.  The fault impedances and current division factor Sf are determined for the worst‑fault type and location, including any conceivable system additions over the next 25 years.  Thus, no additional safety factor for system growth is added.  In addition, it is assumed that the substation will not be cleared by circuit breakers with an automatic reclosuring scheme.  Thus, the fault duration and shock duration are equal.

B1. Square grid without ground rods ‑ example 1
Using the step‑by‑step procedure as described in 16.4 and illustrated in figure 16-1, the following design evaluations can be made.

Step 1: Field data.  Although the substation grounding grid is to be located within a rectangle of 63 m ( 84 m (5292 m2), for the initial design assessment it may be expedient to assume a square 70 m ( 70 m grid with no ground rods.  Consequently, the area occupied by such a grid is A = 4900 m2.  An average soil resistivity of 400 (‑m is assumed, based on soil resistivity measurements.

Step 2: Conductor size.  Ignoring the station resistance, the symmetrical ground fault current If ( 3I0, is computed using equation (65):




(B1)




(B2)

and, hence  (3I0( = 3180 A

Because the fault duration is 0.5 s, according to table 15.1 of Clause 15.10 the decrement factor Df is 1.00; thus, the rms asymmetrical fault current is also 3180 A.  For a conservative design, this current magnitude will be used to determine the minimum diameter of ground conductors.

Assuming the use of copper wires and ambient temperature of 40(C, the simplified equation (41) and table 11.2 of Clause 11 is used to obtain the required conductor cross‑sectional area.  For 0.5 s and using the melting temperature of 1084 (C for hard‑drawn copper, the required cross-sectional area in circular mils is




(B3)




(B4)

Because Ac = (d2/4 the conductor diameter is less than 3.5 mm, or 0.0035 m.

Based on this computation, a copper wire as small as size AWG No 8 could eventually be used, but due to the mechanical strength and ruggedness requirements, a larger (2/0 AWG) conductor with diameter d = 0.0105 m (0.414 in) is usually preferred as a minimum.

Consequently, at this stage, the designer may opt to check if, alternately, the use of a less conductive (30%) copper‑clad steel wire and the imposition of a more conservative maximum temperature limit of 700 (C will still permit the use of a conductor with diameter d = 0.01 m.

Using equation (40) and table 11.1 of Clause 11.3 gives




(B5)




(B6)

In this case, dmin = 4.46 mm, or approximately 0.005 m, which is less than d = 0.01 m desired.  Hence, a 30% copper‑clad steel wire of AWG 2/0 size is a viable alternative for grid wires, even if a conservative maximum temperature limit of 700(C is imposed.

Step 3: Touch and step criteria.  For a 0.102 m (4 in) layer of crushed rock surfacing, with resistivity of 2500 (‑m, and for an earth with resistivity of 400 (-m, the reflection factor K is computed using equation (23) of Clause 7.4:





(B7)




(B8)

Figure 7.6 of Clause 7.4 indicates for K = -0.72 the resistivity of crushed rock is to be derated by a reduction factor C ( 0.74.  The reduction factor C can also be approximated using equation (28) of Clause 7.4:




(B9)




(B10)

Assuming that for the particular station the location of grounded facilities within the fenced property
 is such that the person's weight can be expected to be at least 70 kg, equations (30b) and (32b) may be used to compute the tolerable step and touch voltages, respectively, as follows:

Estep70 =


(B11)




(B12)

Etouch70 = 


(B13)




(B14)

Step 4: Initial design.  Assume a preliminary layout of 70 m (70 m grid with equally spaced conductors, as shown in figure B1, with spacing D = 7 m, grid burial depth h = 0.5 m, and no ground rods.  The total length of buried conductor, L, is 2 ( 11 ( 70 m = 1540 m.

Fig B1
Square grid without ground rods
Step 5: Determination of grid resistance.  Using equation (50) of Clause 14.2, for L = 1540 m, and grid area A = 4900 m2 the resistance is




(B15)




(B16)

Step 6: Maximum grid current IG. Per procedure and definitions of 15.1, the maximum grid current IG is determined by combining equations (61) and (62) of Clause 15.1.  Referring to Step 2, for Df = 1.0, and the given current division factor Sf = 0.6,




(B17)

and



(B18)

Thus,




(B19)




(B20)

Step 7: Now it is necessary to compare the product of IG and Rg, or GPR, to the tolerable touch voltage, Etouch70.



 volts
(B21)

which far exceeds 838 V, determined in Step 3 as the safe value of Etouch7O.  Therefore, further design evaluations are necessary.

Step 8: Mesh voltage.  Using equation (76) of Clause 16.5, Km is computed:




(B22)




(B23)

where




 





and









The factor Ki is computed using equation (78):



(B24)




(B25)

where





















and





Finally, Em is computed using eq. 75 and 79:




(B26)




(B27)

Step 9: Because the estimated mesh voltage is higher than the tolerable touch voltage (that is, 1002.1 V versus 838.2 V), the grid design must be modified.

For comparison, the SGA programs result in 2.67 ohms, 984.3 V and 498.7 V for the grid resistance, touch voltage and step voltage, respectively, for this example.

B2.
Square grid with ground rods ‑ example 2 

In the previous example B1, Step 10 of the design procedure has not been reached due to the failure to meet the criterion of Step 9. Generally, there are two approaches to modifying the grid design to meet the tolerable touch voltage requirements: (1) reduce the GPR to a value below the tolerable touch voltage or to a value low enough to result in a value of Em below the tolerable touch voltage, and (2) reduce the available ground fault current.   Usually, (2) is difficult or impractical to achieve, so the grid is modified by changing any or all of the following: grid conductor spacing, total conductor length, grid depth, addition of ground rods, etc.  In this example, the preliminary design will be modified to include 20 ground rods, each 7.5 m (24.6 ft) long, around the perimeter of the grid, as shown in figure B2, below.

Fig B2 
Square grid with twenty 7.5 m rods
Step 5. Using equation (50) of Clause 14.2, for L = 1540 + 20(7.5 = 1690 m, and A = 4900 m2 yields the following value of grid resistance Rg: 




(B28)




(B29)

Steps 6 and 7. The revised GPR is (1908)(2.75) = 5247 V, which is still much greater than 838.2 V.

Step 8. Using equation (76) of Clause 16.5, Km is computed:




(B30)




(B31)

where





and









This time, Em is computed using Eq. 75 and 79:




(B32)




(B33)

Step 9. Now the calculated corner mesh voltage is lower than the tolerable touch voltage (747.4 V versus 838.2 V), and we are ready to proceed to step 10.

Step 10: Step voltage criterion.  Because the step voltage has not been calculated yet, equations (78), (81) and (82) are used to compute Ki, Es, and Ks, respectively.  Note that the value for Ki is still 1.272 (same as for mesh voltage).




(B34)




(B35)

Then




(B36)




(B37)

Step 11.  The computed Es is well below the tolerable step voltage determined in Step 3 of example 1.  That is, 548.9 V is much less than 2686.6 V.

Step 12 .  A safe design has been obtained.  At this point, all equipment pigtails, additional ground rods for surge arresters, etc., should be added to complete the grid design details.

For comparison, the SGA programs result in 2.52 ohms, 756.2 V and 459.1 V for the grid resistance, touch voltage and step voltage, respectively, for this example.

B3.
Rectangular grid with ground rods ‑ example 3 
In this example the preliminary grid design will be reconciled in terms of the actual shape of the grounding area as an alternative design.  Realizing that the full grounding area is only about 8% larger than that used in the previous calculations, most of the conclusions from example 2 can be used for arriving at a suitable final design solution.

Choosing, again, spacing D = 7 m, for a rectangular 63 m ( 84 m grid, the grid wire pattern is 10 ( 13, and the grid conductor combined length is 13 ( 63 m + 10 ( 84 m = 1659 m.  Assume the use of 38 ground rods, each 10 m long, as shown in figure B3.

Step 5. Again, using equation (50) of Clause 14.2, but for L = 1659 m + (38)(10 m) = 2039 m and A = 63 m ( 84 m = 5292 m2, gives




(B38)




(B39)

Steps 6 and 7. Using IG = 1908 A as before, and RG = 2.62 ohms, the GPR = (1908)(2.62) = 4998.96V, which is much greater than 838.2 V.

Fig B3
Rectangular grid with thirty‑eight 10 m ground rods
Step 8. For the particular design arrangement shown in Fig B3, eq. 75, 76,77 and 79 can again be used to estimate the corner mesh voltage.  However, since the grid is rectangular, the value of n to be used in the mesh voltage computation will be different, based on the factors below.



























Now Km is computed using equation (77) of Clause 16.5:




(B40)




(B41)

where









Equation (77) is used to compute Ki :




(B42)




(B43)

Finally, Em is computed using Eq. 75 and 79:



 
(80)



 
(B81)

Step 9: Touch voltage criterion. This calculated mesh voltage is  well below the Etouch7O limit of 838.2, but uses 119 m of additional conductor and 230 m of additional ground rods, as compared with the previous example.  Thus, the mesh spacing could be reduced, the number and/or length of ground rods could be reduced, or both to achieve the same margin of safety as example B2.

The remaining steps are the same as demonstrated above and will not be repeated here.

For comparison, the SGA programs result in 2.28 ohms, 519.4 V and 349.7 V for the grid resistance, touch voltage and step voltage, respectively, for this example.

B4.
Equally spaced grid with ground rods in two‑layer soil ‑ Exhibit 1
The SGA package of grounding computer programs, described in EPRI's Final Report EL ‑ 2682, Vol. 2, was used to model an equally spaced grid in two‑layer soil.

Fig B4 
Equally spaced square grid with nine rods in two‑layer soil
Fig B5
Diagonal voltage profile for the grid of fig B4 in two‑layer soil
As shown in figure B4, the 61 m ( 61 m (200 ft ( 200 ft) grid consisted of four meshes per side, and had nine ground rods, each 9.144 m (30 ft) long.  The diameter of ground rods was 0.0127 m (0.5 in).  The grid consisted of four meshes per side, formed by wires of a 0.01 m diameter, buried 0.5 m below the earth's surface.  The depth of the upper layer 300 (‑m soil was 4.47 m (15 ft); the lower soil had resistivity of 100 ohm/m.

The computer‑calculated values of resistance, corner mesh voltage, and maximum step voltage, were as follows:

Rg = 1.353 ohms
Em = 49.66% of GPR
Es = 18.33% of GPR

As can be determined from figure B5, the mesh voltage coordinates were X = ‑75.00 ft, and Y= ‑75.00 ft, that is, near the center of the corner mesh.  The maximum step voltage (not shown) was calculated outside the grid, between the grid corner (X, Y = ‑100 ft) and the point at X, Y = 102.12 ft, that is, approximately over 1 m distance in a diagonal direction away from the grid corner.

Fig B6

Unequally spaced square grid with twenty-five 9.144 m rods
B5.
Unequally spaced grid with ground rods in uniform soil ‑ Exhibit 2
The SGA package was also used to model a square grid with unequally spaced conductors, shown in figure B6.

The computer output included the grid resistance, a surface voltage profile, the step voltage because of a more dense spacing between the peripheral conductors, and the corner mesh voltage.

As shown in Fig B7, the corner mesh voltage is only 9.29% of the GPR, while the maximum touch voltage, occurring above the largest interior mesh, is 17.08% of the GPR.

The maximum touch voltage, thus, did not occur in the corner mesh.  For other choices of conductor spacings, the maximum touch voltage may occur above some other meshes.  Therefore, for unequal spacings, the touch voltages must be investigated over the entire grid, and the simplified criterion for checking the corner mesh voltage alone is not sufficient.  On the other hand, the resistance Rg is not too dependent on the exact configuration of grid conductors and ground rods. (For instance, were Rg estimated by equation (50) for a combined length of grid conductors and ground rods L = 18 ( 19.44 m + 25 ( 9.144 m = 1874.5 m, the calculated value of 1.61 ( would be less than 14% higher than the value of 1.416 ( calculated by the computer.)

Fig B7
Diagonal voltage profile for an unequally spaced grid of Fig B6
Annex  C

Graphical and approximate analysis of current division 

(Informative)

C1.  Introduction

A graphical method for determining the maximum grid current, based on results obtained using the SMECC program has been developed. This method attempts to correlate the substation zero sequence fault obtained from a standard short circuit study to the actual current flowing between the grounding system and surrounding earth. The original presentation of this concept was published in /1/. That paper describes the parametric analysis performed and  the resulting basis for the assumptions used to develop the curves. Additional curves have since been developed to address other system configurations. The following is an explanation of the use of the graphs shown in figures C1 through C22.
The graphs are divided into four categories:

a) 100% remote and 0% local fault current contribution, representing typical distribution substations with delta-wye transformer, with X transmission lines and Y feeders (figures C1 through C16)

b) 50% remote and 50% local fault current contribution (figures C17 and C18)

c) 75% remote and 25% local fault current contribution (figures C19 and C20)

d) 25% remote and 75% local fault current contribution (figures C21 and C22)

Categories (2), (3), and (4) represent typical transmission substations or generating plants with X transmission lines(feeders are considered to be transmission lines in these cases), and with local sources of zero sequence current, such as auto transformers, three winding transformers, generators(grounded-wye GSU's), etc.

The following assumptions were used to obtain the graphs:

1) Transmission line length of 23.5 miles and a distance between grounds of 0.0947 miles (500 feet).

2) Transmission tower footing resistance of 15 or 100 .

3) Transmission line structure single pole with 1- 7#10 alumoweld shield wire and 336.4 kcmil, 26/7 acsr conductor.

4) Distribution line length of 2.5 miles and a distance between grounds of 0.0758 miles (400 feet).

5) Distribution pole footing resistance 25 or 200 .

6) Distribution pole  3 phase triangular layout, with one 336.4 kcmil, 26/7 acsr phase and 1/0 acsr neutral conductor.

7) Soil resistivity of 100 -meters.

8) Substation resistances of 0.1, 0.5, 1.0, 5.0, 10.0, and 25.0 .

9) Number of transmission lines varied from 1, 2, 4, 8, 12, and 16.

10) Number of distribution lines varied from 0, 1, 2, 4, 8, 12, and 16. 

11) One remote source for each two(2) transmission lines.

C2  How to use the graphs and equivalent impedance table

On each graph, a family of curves is plotted, with each curve representing a different number of transmission lines and/or feeders. The abscissa  is a range of grounding system impedances from 0.1 to 25.0 ohms. The ordinate is the percent of the total zero sequence substation bus ground fault which flows between the grounding system and surrounding earth.

Table C1 shows the system impedance at 1 .  The magnitude of the equivalent total ground impedance is 
.  From table C1, the equivalent impedance of the line and feeders is 0.54 +j 0.33 , and a feeder footing resistance of 25 , a total fault current of 1600 amperes, transmission footing resistance of 15 . To determine the GPR with current splits, parallel the grid resistance with the appropriate impedance from the table and multiply this value by the total fault current. For example, a substation with 1 transmission line and 2 feeders has a resistance of 5  and feeder pole ground  resistance of 200 .  The second column of impedances is for transmission footing resistance of 100  and feeder pole ground resistance of 25  for 100% remote contribution with X transmission lines and Y feeders.  The first column of impedances is for transmission line tower footing resistance of 15 



 
and the GPR is




 volts

To calculate the grid current, divide the GPR by the resistance.




 Amperes

The grid current may also be computed directly by current division.




 amperes

C3  Examples

To illustrate the use of the graphical analysis, consider the example shown in figure 23.  The SMECC program calculated the maximum grid current of 2,354.6 amperes, with a total bus ground fault of 9,148.7 amperes.  The system in question had two transmission lines with a tower footing resistance of 15.0 .  Figure C4 shows curves for two lines/ two feeders and two lines/ four feeders.  Thus, interpolation was necessary for this example.  From figure C4, we see that the approximate split factor Sf was (32+23)/2 or 27.5%. The maximum grid current was
 and a feeder pole resistance of 25.0 



 Amperes

Using table C1, the equivalent impedance of the system neutral circuit for two lines and two feeders is 0.455 + j0.241 .  The average of the split factors for these two cases will be used.
, and for two lines and four feeders is 0.27 + j0.165 




Thus, Sf = (0.349 +0.247) / 2 = 0.298 or 29.8%

The resulting grid current using this method is




 Amperes

Both methods compare favorably with the value of 2,354.6 amperes or 26% of 3I0 from the program SMECC, though the equivalent impedance method is generally more conservative.

Next consider the more complex system shown in figure C24.  This example is similar to the first, except that the distribution substation is replaced with a local source of generation, such as a cogeneration plant.  For this example, there is both local and remote sources of fault current, so the percent of local vs. remote must be computed.  The SMECC program computed a total fault current of 19,269.6 Amperes at the 115kV bus, with 48.7% contributed by the local source and 51.3% contributed by the remote sources.  The closest curves are for 50/50 split (figure C17).  For a grid resistance of 0.9 ohms, the split factor is determined from the curve for two lines and no feeders - Sf = 29%.  The maximum grid current is




 Amperes

This does not compare as well as the case with 100% remote contribution, but is still better than using the total fault current, or even the remote or local contribution.  For this case, the SMECC program results in a value of 4,034.8 amperes, or 21% of 3I0.  The equivalent impedance method does not work as well for cases other than 100 percent remote contribution, and is not recommended.

C4  Equations for computing line impedances

The following equations are found in the Westinghouse T&D Reference Book, Fourth Edition.[B??   ]  The definitions of the terms used in the equations are:

GMD
is the geometric mean distance between the phase conductors

GMR
is the geometric mean radius of the conductor

dab
=
is the distance between conductors a and b

rc
=
is the ac resistance of the conductor, at frequency f
xa
=
is the inductive reactance of the conductor to one foot spacing, at frequency f

f
=
is the frequency in Hz

De
=
is the equivalent depth of earth return

The positive sequence impedance, Z1, of a transmission line (with earth return), ignoring the effects of overhead static wires, is




  /mile
(C1)

where





The zero sequence self impedance, Z0(a) , of the transmission line (with earth return), with no overhead static wires is




  /mile
(C2)

where





and ra, xa and xd areas defined above using characteristics of the phase conductors.

The zero sequence self impedance, Z0(g) , of one overhead static wire (with earth return) is




  /mile
(C3)

where ra and xa are as defined above using characteristics of the overhead static wire, and re and xe are as defined above.

The zero sequence self impedance, Z0(g) , of two overhead ground wires (with earth return) is




  /mile
(C4)

where





dxy is the distance between the two overhead static wires, ra and xa are as defined above using characteristics of the overhead static wire, and re and xe are as defined above.

The zero sequence mutual impedance, Z0(ag) between one circuit and n ground wires (with earth return) is




  /mile
(C5)

where





dag1 is the distance between phase a and the first overhead static wire, etc., and re and xe are as defined above.

Then, the zero sequence impedance of one circuit with n ground wires (and earth return) is




  /mile
(C6)

These equations for Z1 and Z0 are used, along with appropriate impedances for transformers, generators, etc., to compute the equivalent fault impedance.

To compute the impedance of an overhead static wire or feeder neutral for use in Endrenyi's formula, the simple self impedance (with earth return) of the conductor is used.




  /mile
(C7)

where

ra and xa are as defined above using characteristics of the overhead static wire or feeder neutral, and re and xe are as defined above.

Table C1.

Approximate equivalent impedances of

transmission line overhead static wires and feeder neutrals

NUMBER

OF

TRANSMISSION

LINES
NUMBER

OF

FEEDER

NEUTRALS
LINE RTFR = 15

LINE RTFR = 25

R + jX ()
LINE RTFR = 100

LINE RTFR = 200

R + jX ()

1
1
0.91 + j.485
3.27 + j.652

1
2
0.54 + j0.33
2.18 + j.412

1
4
.295 + j0.20
1.32 + j.244

1
8
0.15 + j0.11
.732 + j.133

1
12
0.10 + j.076
.507 + j.091

1
16
.079 + j.057
.387 + j.069

2
1
.685 + j.302
2.18 + j.442

2
2
.455 + j.241
1.63 + j.324

2
4
0.27 + j.165
1.09 + j.208

2
8
0.15 + j0.10
.685 + j.122

2
12
0.10 + j0.07
0.47 + j.087

2
16
0.08 + j.055
.366 + j.067

4
1
0.45 + j0.16
1.30 + j.273

4
2
0.34 + j0.15
1.09 + j 0.22

4
4
0.23 + j0.12
.817 + j0.16

4
8
.134 + j.083
.546 + j.103

4
12
.095 + j.061
0.41 + j.077

4
16
.073 + j0.05
.329 + j0.06

8
1
0.27 + j0.08
0.72 + j.152

8
2
0.23 + j0.08
0.65 + j.134

8
4
0.17 + j.076
.543 + j0.11

8
8
.114 + j.061
.408 + j.079

8
12
.085 + j.049
.327 + j.064

8
16
.067 + j.041
.273 + j.052

12
1
.191 + j.054
.498 + j.106

12
2
0.17 + j.055
.462 + j.097

12
4
0.14 + j.053
.406 + j.083

12
8
.098 + j.047
.326 + j.066

12
12
.077 + j.041
.272 + j.053

12
16
.062 + j.035
.234 + j.046

16
1
.148 + j0.04
.380 + j.082

16
2
.135 + j.041
.360 + j.076

16
4
.113 + j.041
.325 + j.067

16
8
.086 + j.038
.272 + j.055

16
12
.068 + j.034
.233 + j.047

16
16
.057 + j0.03
.203 + j.040

1
0
2.64 + j0.60
6.44 + j1.37

2
0
1.30 + j0.29
3.23 + j0.70

4
0
.65 + j.15
1.61 + j.348

8
0
.327 + j.074
.808 + j.175

12
0
0.22 + j.049
.539 + j.117

16
0
.163 + j.037
.403 + j.087

0
1
1.29 + j.967
6.57 + j1.17

0
2
.643 + j.484
3.29 + j0.58

0
4
.322 + j.242
1.65 + j.291

0
8
.161 + j.121
.826 + j.148

0
12
.108 + j.081
.549 + j.099

0
16
.080 + j.061
.412 + j.074

Annex  D

Simplified step and mesh equations

(Informative)
In the previous editions of this guide, the following equation was provided for determining the value of a mesh voltage (in volts) on the earth's surface above the center of a corner mesh ‑ assuming an equally spaced rectangular grid, which is buried in depth h in a homogeneous soil of uniform resistivity.  This grid may consist of n parallel conductors spaced D apart, and of an undetermined number of cross connections.  All grid wires are assumed to be of diameter d. The spacing of parallel conductors D, as well as d and h, are in meters.





(D1)

where

-m

is the average soil resistivity in 
I
is the maximum rms current flowing between ground grid and earth

L
is the 
total length of buried conductors, including cross connections, and (optionally) the combined length of ground rods in m

Ki
is the corrective factor for current irregularity

Km
is the mesh factor defined for n parallel conductors,

Reference [B1] derived the factors Km and Ki to account for the geometry of the grounding system.  Sverak [B131] modified the factor, and added the factors Kii and Khin an attempt to improve the accuracy of the results.  The relationship between Km and Em depends largely on the current density in the perimeter conductors versus the current density in the inner conductor.  To reflect this effect of current density and to correct some of the deficiencies in the equation for Km, Sverak added the weighing terms, Kii and Kh into the equation for Km.  The resulting equation for Km was more accurate and versatile than previous forms of the equation:





(D2)

where

Kii
is 1 for grids with ground rods along the perimeter, or for grids with ground rods in the grid corners, as well as both along the perimeter and throughout the grid area,

or, for grids with no ground rods or grids with only a few ground rods, none located in the corners or on the perimeter.




(D3)




(D4)

ho
is 1 m (reference depth of grid)

Because of assumptions made in the derivation of Km, a corrective factor Ki is needed to compensate for the fact that the subject mathematical model of n parallel conductors cannot fully account for the effects of a grid geometry; that is, for two sets of parallel conductors that are perpendicular to each other and interconnected at the cross connection points. For a large number of square and rectangular grids, the mesh voltage was obtained using a computer.  From this computer generated data, a new expression for Ki was found to better fit in the mesh voltage equation. [B??] (Reference Baldev Thapar, "Simplified Equations for Mesh and Step Voltages in an AC Substation," IEEE Transactions on Power Delivery, vol 6, no 2, April 1991.)  This factor is:





(D5)

I  The simplified Em equation used in the previous edition of the guide has been limited to square and rectangular grids with square meshes.  In practice, a large number of grounding grids have shapes other than square or rectangular.  While the specific formula for Km has remained the same as the 1986 edition of the guide, a new value of n based on the geometry of the grid and the geometry of the meshes was developed in [B?? Thapar] to allow the equations to be effective for a variety of grid shapes, including symmetrical T-shaped, triangular, and L-shaped grids.





(D6)

where





Lc
is the total length of the conductor in the horizontal grid, m

Lp
is the peripheral length of the grid, m

A
is the area of the grid, m2
Lx
is the maximum length of the grid in the x direction, m

Ly
is the maximum length of the grid in the y direction, m

Dm
is the maximum distance between any two points on the grid, m

While these changes to the equations did expand their use to include a variety of practical ground grid shapes, they did not include the use of ground rods.  An attempt was made to expand these equation to include the use of ground rods.  If LC represents the total grid conductor length, LR represents the total length of all ground rods, and Rl represents the average length of each ground rod, then for grids with ground rods in the corners, as well as along the perimeter and throughout the grid.





(D7)

The multiplier for LR is an empirical function that reflects the fact that the current density is higher in the ground rods than in the horizontal grid conductors for uniform soil.

In the previous editions of this guide, the following equation was provided for determining the value of the worst case step voltage (in volts)





(D8)

where

-m

is the average soil resistivity in 
I
is the maximum rms current flowing between ground grid and earth

L
is the total length of buried conductors, including cross connections, and (optionally) the total effective length of ground rods in m

Ki
is the corrective factor for current irregularity

Ks
is the mesh factor defined for n parallel conductors,

Sverak has derived a factor Ks, based on the geometry of a ground grid with no ground rods. [B??] (reference Sverak paper).  As with the mesh voltage, this Ks is proportional to the step voltage Es.  Again, computer simulations were used to derive empirical factors to improve the accuracy of previous versions of Es. [B??] (Thapar)




(D9)

where n, D and h are defined above.

While these changes to the equations did expand their use to include a variety of practical ground grid shapes, they did not include the use of ground rods.  An attempt was made to expand these equation to include the use of ground rods.  If LC represents the total grid conductor length and LR represents the total length of all ground rods, then for grids with or without ground rods,





(D10)

These new simplified equations were compared to computer solutions for hundreds of different ground grids and the results were similar to those calculated by the more rigorous computer programs in most cases.

Annex  E

Equivalent uniform soil model for non-uniform soils

(Informative)

In the interest of simplicity, several assumptions have been made in developing the ground grid design equations of this guide.  One such assumption is that these equations accept only a uniform soil resistivity model regardless of the soil under consideration.  The survey, done among the guide users, indicated the need to provide a guideline for representing a soil regardless of its type by a uniform equivalent and, thus, remove this limitation in the use of the design equations.

A typical soil has several layers, each having a different resistivity.  Most often lateral changes also occur, but in comparison to the vertical layers, these changes usually are more gradual.  Station sites where the soil may posses uniform resistivity throughout the area and to a considerable depth are seldom found.  A uniform soil interpretation of apparent resistivities obtained in the field, under these circumstances, is the most difficult  task to perform even with the help of computers.  Accordingly, it must be recognized that the soil model is only an approximation of the actual soil conditions and that a perfect match is unlikely.  However, it has been recognized that the two layer representation of a soil is closer to the actual soil conditions compared to its uniform equivalent.

Sometimes, in a multi-layer soil, the variation in apparent  soil resistivity a with respect to depth or pin spacing is not too great.  Such a soil can be represented as a uniform soil with a single soil resistivity value.  Although it is difficult to draw a clear line to indicate whether the soil is uniform or not, the approach taken by the task force consisted of defining the uniform soil based on the two layer equivalents of several field measured resistivity profiles.  EPRI's SOMIP program was employed to compute two layer equivalents of these soils.  The guideline, evolved as a result of this approach, says that a soil can be represented as a uniform soil if the difference between two extreme values of apparent resistivity is less than 30 percent of the larger resistivity value.  Once the soil is determined to be a uniform soil, the average apparent resistivity value computed from equation (E1), then represents that soil in the design equations.




(E1)

Where -m.
a(n) are the apparent resistivity measurements obtained at n different spacing in four-pin method or at n different depths in driven ground rod method in a(3) --- a(2), a(1), 
A majority of the soils will not meet the above criteria for the uniform soil.  To determine uniform soil models to represent non-uniform soils, the task force took the similar approach.  The measured apparent resistivity data from several sites were interpreted by three different soil models.  Each soil was interpreted by the two-layer soil model computed with the SOMIP program and two different uniform soil models: one determined from equation (E1), and the other determined from equation (E2).




(E2)

Where

-m.
a(max)
is the maximum apparent resistivity value (from measured data), 
-m.
a(max)
is the minimum apparent resistivity value (from measured data), 

The next step was to compute the ground grid resistance Rg, the corner mesh voltage Emesh, and the corner step voltage Estep  for a typical ground grid using EPRI's SGSYS program.  A 250'X250' ground grid with 64 meshes and uniformly distributed ground rods was selected for this investigation.  The length of the ground rods, modeled in SGSYS, varied from one soil case to another.  For a given soil case, this length was determined so as to reach the depths (or pin spacings) where a(av2) occur in the measured apparent resistivity profile.  Figure-E1 illustrates the modeled ground grid including the locations for computed step and touch voltages.
a(av1) and 
Figure-E1   The ground grid modeled in SGSYS for computing grounding parameters

Following the computations, the grounding parameters computed with the two layer model were compared with those computed using the uniform soil models. This comparison indicated that the mesh and step voltages computed with the soil model represented by a(av2) yielded conservative values compared to those computed with the two layer soil model for a majority of investigated soils.

Table E1 presents the comparison of grounding parameters computed using the two layer soil model with those computed using the uniform soil model represented by a(av2) for two typical soils.  These soil types including their apparent resistivity profiles are the same ???as shown in Annex??-    (Annex on Benchmark Cases) and are shown in table-E2 and table-E3 in this Annex.

Table-E1  Ground parameters computed with two layer soil compared with those computed with equivalent uniform soil model

Soil Type
Computed Grounding Parameters with Two Layer Soil Model



Computed Grounding Parameters with Uniform Soil Model





2, h1, 
-m,ft.-m,
Rg

Em Volt
Es
Volt
(av2)
-m
Rg

Em Volt
Es
Volt

1
100,300,20
1.28
126
85
158
0.89
151
86

2
300,100,20
0.72
187
92
194
1.09
185
106

Table E2  Apparent resistance data for soil type-1 and 2 of table E1, measured with 4-pin method

Probe Separation (ft)
Soil Type-1, Resistance ,
Soil Type-2, Resistance ,

1.0
29.725
89.16

3.0
15.325
45.845

5.0
9.969
29.553

15.0
3.853
9.385

20.0
3.152
6.462

30.0
2.49
3.517

50.0
1.897
1.504

70.0
1.557
0.897

90.0
1.321
0.642

110.0
1.146
0.505

130.0
1.011
0.419

150.0
0.904
0.359

Annex  F

Grounding Methods for High‑Voltage Stations With Grounded Neutrals
(Informative)
(Erdungsmassnahmen fur Hochstspannungsanlagen mit Geerdetem Sternpunkt)

Walter Koch.
 Elektrotechnische Zeitschrift.

Vol. 71, No. 4, pp. 89‑91, Feb. 1950

It is not economically feasible to provide grounding in high‑voltage stations with grounded neutral, which will in to limit contact potentials to ground electrodes and the connected apparatus to less than 125 volts.  One has to deal with a multiplicity of potentials which may be established between the plant and the surroundings under Short-circuit conditions.

Experiments with models show that by making the ground system in the form of a grid, areas within the system can be produced which will be safe.  Means for safe entry into the grounding area will be given.

With a directly grounded neutral point there flows into the system at the fault point the so‑called ground‑fault current instead of the total single‑phase short-circuit ground current (Ungrounded System).  This ground‑fault current depends upon the generating capacity of the power plants in the area and on the impedance of the ground circuit.  The grounding systems of a solidly grounded network will carry a portion of the ground‑fault current which may be a minimum for faults a great distance from the station and may be a maximum, namely the total ground‑fault current, for a fault in the station.

While the grounding systems may be adjusted to eliminate dangerous contact potentials by suppression of ground short‑circuit currents, this is not usually demanded of solidly grounded neutral systems because it does not appear to be practicable.  For ground‑fault currents above 1000 amperes, grounding systems of vast dimensions must be installed in order to meet the usual 125‑volt contact potential requirement.  A numerical example will show this.  The surface area of an outdoor substation may be 250 · 250 meters.  Here one has the possibility of placing a ground plate of 62,500 square meters under the station.  With an average ground resistivity of 100 ohm‑meters and the equivalent circular plate diameter of 280 meters the ground resistance is




or




With such a ground, a ground‑fault current of 5000 amperes will produce a 900-volt potential above the more‑distant surroundings which is many times the potential allowed by VDE.  In spite of this, it has the indisputable advantage that the entire station on this metal plate will have no potentials between parts within itself that are worth mentioning.  For persons inside the station there will not be the slightest danger from undue contact potentials at such a high current.  There would be danger only if at the moment of fault one were to enter or leave the plant or touch it from the outside.  It is not practical to construct such a ground plate.  However, in order not to endanger the personnel of an electrical plant, ways must be sought to fulfill this requirement.

Besides the dangers to personnel, there will be some to the material of the control and communications equipment if it is not provided against.  The sheaths of the control cables provide a connection between the controlled apparatus in the high‑voltage bays and the control point.  Thereby, a fault to ground in the station can cause a very large current to flow through the sheath and melt it.  Communication cables which leave the plant will also conduct ground currents away since intentionally or unintentionally they come into contact with building construction parts.  Thereby, the sheaths acquire the high potential of the station in their vicinity while the conductors approximate the potential of the more-distant surroundings, so that insulation failures may occur.  So likewise the cables of the low‑voltage plant, and the windings of control motors among others may be endangered by large potential differences.  Indeed, for these reasons it is not permissible to rely only on a sufficient interconnection of all apparatus such as circuit breakers, transformer cases, frame parts, etc.  To this all cable sheaths within the plant must also be connected; so likewise the control mechanisms in the switching station to which the control cables are connected.  Basically the entire plant should be provided with a built‑up ground mat for the ground‑fault current, to which all equipment parts in the plant are connected.  So likewise the existing neutral conductors of independent low‑voltage systems should be tied to the ground mat.  By this method there will be the least worry that significant potential differences will arise between the accessible metallic parts of the plant and the plant equipment so protected will be safe from failure.

Now, it is certain that considerable and therefore dangerous potentials can arise between the soil, the floors of buildings on one side and the metallic parts of the plant during the time of faults.  Therefore one must also consider the safety of operating personnel who in the course of their work must touch such metal parts.  For this purpose the operating position may be provided either with an insulated floor capable of withstanding the high potential or with a metallic grid in the floor and tied to the ground mat or provided with both.  Such metallic foot grids have been previously used for protection in Siemens-Schuckert plants with ungrounded star neutral.  They consisted of small meshed wire netting cemented into the floor and tied to the grounding system, and provided absolute protection to persons standing thereon and grasping operating controls in that a highly conducting shunt path was provided between hands and feet.

As mentioned in the introduction, a large metallic plate is a suitable protection against all step potentials and contact potentials within the plant.  Since such a metallic plate installation is not realizable, the question arises on how far one can go in substituting a network of ground straps and the necessary mesh spacing in order to obtain tolerable potential differences.

The investigation of the potential distribution of complicated ground electrode arrangements, which such a ground mat is, is not possible by computation, since one can derive formulae only for simple electrode shapes and even simple combinations of these electrode shapes are not amenable to calculation.  For mesh‑type electrode arrangements with irregular depth of burial which is the way they are used for the purpose of potential control and other complicated grounding structures, one is led to the use of models.  For this purpose such model measurements using an electrolytic tank were undertaken.  A metal container filled with a conducting solution served as the semi‑infinite space for the current diffusion.  Figure F1 shows the circuit of the test arrangement.  The potential distribution for model M can be obtained by a null method using the electrode S, the calibrated potentiometer P and telephone receiver T. In order to reduce the electrolytic effect of the chopped direct current supply on the model, a slowly rotating switch U was placed in the direct current supply leads.

The model of the ground mat consisted of a copper wire 0.2 millimeters in diameter arranged in a square with 120 millimeter sides and set on the surface.  For the usual ground straps with a cross‑section of 30 · 3 millimeters corresponding to an equivalent diameter of 23 millimeters this model represented a replica of a ground system with a length of

Figure F1
Circuit for obtaining potential distribution
Figure F2

Measured potential distribution for various ground mats
Figure F3

Measured potential distribution for various ground mats



or 13.8 meters on a side.  After obtaining the potential distribution, the square was subdivided to contain four squares by the addition of a wire cross, the four subsquares were similarly subdivided until 64 subsquares were attained and in each case the potential inside the square was measured.  As the mesh becomes finer the effect approaches a plate electrode.  In figures F2 - F5 the potential at the center point of each square is given in percent of the potential of the ground mat.  The potential differences which characterize the step potentials and thereby the hazard are according to these figures for fine‑mesh electrodes 11 ‑ 20 percent of the total potential.  The mesh spacing of the mat with 64 meshes is, according to the above‑mentioned model scale, 13.8/8 = 1.7 meters.  The potential distributions in cross‑sections through the mats at A‑B, C‑D, E‑F and G‑H of figures F2 -- F5 are shown in figure F6. In order to determine the effect of only a partial fine mesh inside the outer edge, the arrangement shown in figure F7 was investigated and as shown in figure F8 with further subdivision of a single mesh.  From this it follows that in the area of a fine mesh the same relations (proportions) hold as in the complete meshing of the total grounding area.  The still finer subdivision of a single mesh results in a further raising of the potential inside the mesh, that is, a corresponding decrease of the potential differences and thereby the step potential.

Figure F4
Measured potential distribution for various ground mats
Figure F5
Measured potential distribution for various ground mats
Figure F6
Potential distribution for a ground mat with various mesh densities
ground mat potential = 100 percent
The measurements show, as might be expected, that by using a fine mesh a considerable reduction in potential differences within the mat area can be obtained. Further, it is apparent that small protected areas can be produced by partial matting without completely matting the entire grounding area.  Practical application of such finer meshing can be found principally in outdoor stations in the neighborhood of accessible equipment where the hazard is greatest.

A reduction of the effect, which will not completely eliminate potential differences, can be arrived at by a fill of course grit (gravel) to a depth of about 1 centimeter over such a ground grid.  With this everything practical has been done in order to minimize the hazard, if not to eliminate it entirely.

To be sure, there remain the locations of the passageways to the protected areas which remain a hazard when traveling over them during the time of a fault.  F6 shows the high potential drops at the edges of the wide meshed areas, where step potentials of about 45 percent of the total potential to the ground electrode can be encountered.  If one must obtain absolute safety, then on the passageways one must resort to the so‑called potential ramps in order to obtain a small, and as far as possible, uniform potential drop.  Wooden passageways have likewise already been used in the Siemens-Schuckert works in 200‑kV stations.

Figure F7
Potential distribution for ground mats with fine meshes in portions
Figure F8
Potential distribution for ground mats with fine meshes in portions
The means of potential control through grounding straps buried at progressively deeper depths is shown in principle in figure F9, the effectiveness of which was proved by the leveling off of the potential surface in a model.  figure F10 shows the application of potential control around the footing of a tower when one does not desire to, or is not able to, employ a fence.

The magnitude of the expected step potential for a ground mat depends upon the ground resistance, the short‑circuit current and the mesh density.  If one takes the area of an outdoor substation 250 meters square, then a ground strap around the periphery will be 1000 meters long.  Without regard to the cross connections and matted grounds, the ground resistance of this strap is R = _/_L ln 2L/d; where _ is the ground resistivity (generally 100 ohm‑meters) L is the length of the strap in centimeters and d is the equivalent diameter of the strap as a conductor with a semicircular cross‑section (for the usual ground‑strap d = 2.3 centimeters).  With these figures R=0.36 ohm.  The resistance is thus only twice as great as for a solid plate 250 · 250 meters.  The reactance will be reduced by the cross‑connections which are required for tying in the apparatus to be grounded.

With a short‑circuit current of, for example, 5000 amperes, the voltage to the ground system will be about 1800 volts.  With a ground rating as shown in figure F5 the greatest step potential to be expected will be about 11 ‑ 12 percent of this value, or 200 volts, the effect of which on persons can be reduced effectively by using gravel fill.  According to figure F8, with a mesh spacing of 0.85 meters the potential inside the mesh is 7 percent of the ground mat potential and for a ground mat potential of 1800 volts the step potential can thereby be reduced below 125 volts if necessary.

Figure F9
Potential distribution in a ground mat with ramp
(Curve 1) and without ramp (Curve 2)
The systematic application of the protective measures described makes the separation of the operating ground from the protective ground superfluous.  The separation of operating and protective grounds gives no protection for faults inside the station and from experience these must be considered.  The installation of a separated star neutral ground system requires a tremendous amount of land outside the station.  There is no advantage worth mentioning for this since a protective ground is still required inside the station.  It therefore can only be recom​mended that the star‑neutral point be connected to a suitable ground system as described in the foregoing or otherwise for a separate grounding system to employ the requisite materials for an ample development of the protective ground system.

Figure F10
Potential distribution around a mast footing in the direction A‑B

for a mast with ramp (Curve b) and without ramp (Curve a)
Tying together both systems (protective and operating) has the noteworthy advantage that for a ground fault within the station the ground‑fault current component of the faulted station need not be carried by the ground mat but is conducted directly over the grounding conductors which are tied to the star neutral point.  Also, one has only to reckon with the difference between the total ground‑fault current and the station component, whereby there is a considerable reduction in ground mat potential and step potential.

The overhead ground wire of the outgoing station transmission lines may be advantageously connected to the station ground, and effectively reduce the total ground resistance; this is especially so where the ground wire which appears to be necessary for star neutral grounded systems with high ground‑fault currents is of ample design.

SUMMARY
Large contact and step potentials under fault conditions must be considered in high‑voltage stations using grounded star neutral point.  Potential differences which may endanger cable insulation and low‑voltage apparatus and facilities (for example, windings of control motors) may be eliminated by metallic interconnection of equipment housing, sheaths of control and service cables and their neutral conductors, and the construction parts in the control house.  For protection of personnel at the danger points, narrow meshed ground mats with mesh spacing of about 1 meter will serve.  The potential distribution of such ground mats may be investigated by means of electrolytic tanks.  A separate operating ground for the star neutral point is not recommended, since connection of the latter to a general ground system designed according to the viewpoint outlined herein, has advantages over separation.  Approaches to parts of the ground system which have potential control can be made safe by the so‑called potential ramps.

Annex  A

Bibliography

(Informative)

[B1] AIEE Working Group on Substation Grounding Practices.  Application Guide on Methods of Substation Grounding.  AIEE Transactions, vol 73, part 111‑A, 1954, pp 271‑278.

[B2] Analysis Techniques for Power Substation Grounding Systems EPRI Final Report El,‑2682, vols 1 and 2, Oct 1982.

[B3] Armstrong, H. R., Grounding Electrode Characteristics from Model Tests. AIEE Transactions, vol 72, part III, 1953, pp 1301 ‑ 1306.

[B4] Armstrong, H.R., and Simpkin, L. J., Grounding Electrode Potential Gra​dients from Model Tests.  IEEE Transactions on Power Apparatus and Systems, Oct 1960, pp 618-623.     Not found in guide.
[B5] Barbeito, N., Substation ground Grid Tests: Presented at the Southeastern Electric Exchange, June 1-3, 1988

[B6] Barbeito, N., “Substation Ground Grid Tests”, Southeastern Electric Exchange Conference, June 2, 1988.
[B7] Bellaschi, P. L., Lightning Currents in Field and Laboratory.  AIEE Transactions, vol 54, 1935, pp 837‑843.

[B8] Biddle, James, G., Company, Getting Down to Earth, Manual on Earth Resistance Testing (25T), 1970

[B9] Biegelmeier, U. G., Die Bedeatung der Z‑Schwelle des Herzkammerfilim​merns fur die Festlegung von Beruhrunggsspanungs greuzeu bei den Schutzma Bradhmer gegen elektrische Unfate.  E&M, vol 93, no 1, 1976, pp 1‑8.

[B10] Biegelmeier, U. G., and Rotter, K., Elektrische Widerstrande und Strome in Merischlicken Korper.  E&M, vol 89, 1971, pp 104‑109.

[B11] Biegelmeier, U. G., and Lee, W. R., New Considerations on the Threshold ot Ventricular Fibrillation for AC Shocks at 50 ‑ 60 Hz, Proceedings of the IEEE, vol 127, 1980, pp 103 ‑110.

[B12] Blattner, C. J., Study of Driven Ground Rods and Four Point Soil Resistivity Tests, IEEE Transactions on Power Apparatus and Systems, vol PAS‑101, no 8, Aug 1982, pp 2837‑2850.  Not found in guide.
[B13] Blattner, C. J., “Analysis of Soil Resistivity Test Methods in Tow-Layer Earth, IEEE Transactions, Vol., 104, No. 12, December 1985

[B14] Blattner, C.J., and Dawalibit, F., “Earth Resistivity Measurement Interpretation Techniques”, IEEE Transactions, Vol., 103, No. 2, February, 1984

[B15] Blattner, C. J., “Prediction of Soil Resistivity and Ground Rod Resistance for Deep Ground Electrodes”, IEEE Transactions, Vol. 99, No. 5, September/October, 1980

[B16]  Blattner, C. J., “Study of Driven Ground Rods and Four Point Soil Resistivity Data, IEEE Transactions, Vol. PAS 101, No. 8, pp 2837-2850, August, 1982

[B17] Bodier, M. G., La Secrites des Personnes et la Question des Mises a la Terre dans les Postes de Distribution, Bulletin de la Societe' Francaise des Electriciens, ser 6th, vol VII, no 74, Oct 1947, pp 545-562.

[B18] Bodier, M. G., Systematic Investigation of Potential Gradients In and Around a Transformation Substation.  Bulletin de la Societe' Francaise des Electriciens, July 1951.

[B19] Bogajewski, W., Dawalibi, F., Gervais, Y., and Mukhedkar, D., Effects of Sustained Ground Fault Current on Concrete Poles.  Paper 81 WM 202‑1, presented at the IEEE‑PES Winter Meeting, Atlanta, GA, Feb 1981.

[B20] Carson, J. R., Wave Propagation in Overhead Wires with Ground Return. Bell Systems Technical Journal, vol 5, 1926.

[B21] Clem, J. E., Reactance of Transmission Lines With Ground Return.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑50, Sept 1931, pp 901 ​918.

[B22] Computation of Zero Sequence Impedances of Power Lines and Cables.   Engineering Report no 37, Joint Subcommittee on Development and Research of EEI and Bell Telephone Systems, July 22, 1936.

[B23] Conversion Subcommittee of AIEE Substations Committee.  Recommended Grounding Practices for Single Polarity DC Structures.  Paper no 57‑719, AIEE Transactions, vol 76, part III, 1957.

[B24] Crawford, E., and Griffith, M., A Closer Look at "The Facts of Life" in Ground Mat Design.  IEEE Transactions an Industry Applications, vol IA‑ 15, no 3, May/June 1979, pp 241‑250.

[B25] Currents in Earth Wires at the Top of Pylons and  Their Effect on the Poten​tials of the Pylons and Stations in the Neighborhood of a Point of Short‑Circuit to Earth. Contribution no 78, CCITT, Study Group V, Nov 1963.

[B26] Dalziel, C. F., A Study of the Hazards of Impulse Currents.  AIEE Trans​actions, vol 72, part III, Oct 1953, pp 1032‑1043.

[B27] Dalziel, C. F., Dangerous Electric Currents.  AIEE Transactions, vol 65, 1946, pp 579‑585, 1123-1124.

[B28] Dalziel, C. F., Effect of Wave Form on Let‑Go Currents.  AIEE Transactions, vol 62, 1943, pp 739‑744.

[B29] Dalziel, C. F., Electric Shock Hazard.  IEEE Spectrum, Feb 1972, pp 41‑50.

[B30] Dalziel, C. F., Threshold 60‑Cycle Fibrillating Currents. AIEE Transactions, vol 79, part III, 1960, pp 667‑673.   Not found in guide.
[B31] Dalziel, C. F., and Lee, R. W., Reevaluation of Lethal Electric Currents. IEEE Transactions on Industry and General Applications, vol IGA‑4, no 5, Oct 1968, pp 467‑476.

[B32] Dalziel, C. F., Temporary Paralysis Following Freezing to a Wire.  AIEE Transactions, vol 79, part III, 1960, pp 174‑175.

[B33] Dalziel, C. F., Lagen, J. B., and Thurston, J. L., Electric Shock.  AIEE Transcations, vol 60, 1941, pp 1073‑1079.

[B34] Dalziel, C. F., and Lee, W. R., Lethal Electric Currents.  IEEE Spectrum, Feb 1969, pp 44‑50.

[B35] Dalziel, C. F. and Mansfield, T. H., Effect of Frequency on Perception Currents. AIEE Transactions, vol 69, 1950, pp 1161 1168.

[B36] Dalziel, C.F., and Massogilia, F.P., Let-Go Currents and Voltages. AIEEE Transactions, vol 75, part II, 1956, pp 49‑56.

[B37] Dalziel, C.F., Ogden, E., and Abbott, C.E., Effect of Frequency on Let-Go Currents, AIEE Transactions, vol 62, Dec 1943, pp 745-750 and 1000.

[B38] Dawalibi, F., and Mukehedkar, D., Ground Fault Current Distribution in Power Systems--The Necessary Link. Paper A77 754-5, presented at the IEEE Summer Power Meeting, Mexico City, 1977.    Not found in guide.
[B39] Dawalibi, F., Ground Fault Current Distribution Between Soil and Neutral Conductors.  IEEE Transactions on Power Apparatus and Systems, vol PAS-99, no 2, Mar/Apr 1980, pp 452-461.

[B40] Dawalibi, F., Boucimd, M., and Mukhedkar, D., Survey on Power System Grounding Design Practices.  IEEE Transactiorns on Power Apparatus and vol PAS‑99, no 4, July/Aug 1980, pp 1396‑1405.

[B41] Dawalibi, F., and Mukhedkar, D., Influence of Ground Rods on Ground​ing Systems. IEEE Transactions on Power Apparatus and Systems, vol PAS‑98, no 6, Nov/ Dec 1979, pp 2089‑2098.    Not found in guide.
[B42] Dawalibi, F., and Mukhedkar, D. Optimum Design of Substation Ground​ing in Two‑Layer Earth Structure; Part I ‑ Analytical Study, Part 11 ‑ Compari​son Between Theoretical and Experimental Results, and Part Ill ‑ Study of grounding grids Performance and New Electrodes Configuration.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑94, no 2, Mar/Apr 1975, pp 252-261, 262-266, 267-272.

[B43] Dawalibi, F., and Mukhedkar, D., Parametric Analysis of Grounding Systems. IEEE Transactions on Power Apparatus and Systems, vol PAS‑98, no 5, Sept/Oct, 1979, pp 1659‑1668.

[B44] Dawalibi, F., Mukhedkar, D., and Bensted, D., Soil Effects on Ground Fault Currents.  IEEE Transactions on Power Apparatus and Systems, vol PAS​100, July 1982, p 3442.

[B45] Dawalibi, F. P., Southey, R. D, and Baishiki, R. S. "Validity of Conventional Approaches for Calculating Body Currents Resulting From Electric Shocks". IEEE Transactions on Power Delivery, Vol.5, pp 613-626. 1990

[B46]  Dawalibi, F. P., Xiong, W., and Ma, J. "Effects of Deteriorated and Contaminated Substation Surface Covering Layers on Foot Resistance Calculations". IEEE Transactions on Power Delivery, Vol.8, pp 104-113, 1993

[B47]  Dawalibi, F. P., and Ma, J., and Southey, R. D., “Behavior of Grounding Systems in Multilayer Soilers: A Parametric Analysis” IEEE/PES Winter Power Meeting, Paper 93 EM 12202 PWRD, 1993

[B48] Dawalibi, F., and Barbeito, N., “Measurements and Computations of the Performance of Grounding Systems Buried inMultilayer Soils”, IEEE Transactions, Vol. 6, No. 4 pp 1483-1490, October 1992

[B49] Deri, A., Tevan, G., Semlyen, A., and Castanheira, A., The Complex Ground Return Plane ‑ A Simplified Model for Homogeneous and Multilayer Earth Return.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑100, no 8, Aug 1981, pp 3686‑3693.

[B50] Desieno, C. F., Marchenko, P.P., and Nassell, G.S., General Equations for Fault Currents in Transmission Line Ground Wires.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑89, Nov/Dec 1970, pp 1891‑1900.

[B51] Dick, E. P., Fujinmoto, N., Ford, G. L., and Harvey, S., Transient Ground Potential Rise in Gas‑Insulated Substations ‑ Problem Identification and Mitigation. IEEE Transactions on Power Apparatus and Systems, vol PAS 101, no 10, Oct 1982, pp 3610-3619.

[B52] Dick, W. K., and Holliday, H. R., Impulse and Alternating Current Tests on Grounding Electrodes in Soil Environment.  IEEE Transactions on Power Apparatus and Systems, vol PAS-97, no 1, Jan/Feb 1978, pp 102‑108.

[B53] Dodds, T. H., and Spindle, H. E., Grounding of Gas Insulated Substations. IEEE Transactions on Power Apparatus and Systems, vol PAS‑94, no 4, July/Aug 1975, pp 1183‑1191.

[B54] Elek, A., Hazards of Electric Shock at Stations During Fault and Method of Reduction.  Ontario Hydro Research News, vol 10, no 1, 1958, pp 1‑6.

[B55] Endrenyi, J., Fault Current Analysis for Substation Grounding Design. Ontario Hydro Research Quarterly, 2nd Quarter, 1967.

[B56] Endrenyi, J., Analysis of Transmission Tower Potentials During Ground Faults. IEEE Transactions on Power Apparatus and Systems, vol PAS‑86, Oct 1967, pp 1274‑1283.

[B57]  Endrenyi, J., “Evaluation of Resistivity Test for Design of Station Grounds in Non-Uniform Soil”, IEEE Transactions on PAS, Vol. 84, pp 996-970, December, 1963

[B58] EPRI Transmission Line Reference Book 345 kV and Above.  Electric Power Research Council, Palo Alto, CA, 1975.

[B59]  EPRI EL2683, Analysis Techniques for Power Substation Grounding Systems, Georgia Institute of Technology, July, 1992

[B60]  EPRI EL-3982, Soil Resistivity Tests Using Modeling Techniques Ohio State University, May, 1985

[B61]  EPRI EL-2699  Transmission Line Grounding; Safe Engineering Services, Chapter 4, (Resistivity) and Chapter 9 (Field Measurement Techniqes), October, 1982

[B62]  EPRI TR-100863, Seasonal Varations of Grounding Parameters by Field Tests,  July, 1992

[B63] Ewy, K. A., and Smolleck, H. A., A Graphical Explanation of the Resist​ance and Surface‑Potential Calculations for Grounding Systems in Two‑Layer Earth.  Paper 83 SM 430‑6, presented at the 1983 IEEE‑PES Summer Power Meet​ing, Los Angeles, CA.    Not found in guide.
[B64] Fagan, E. J., and Lee, R. H., The Use of Concrete‑Enclosed Reinforcing Rods as Grounding Electrodes.  IEEE Transactions on Industry and General Applications, vol IGA‑6, no 4, July/Aug 1970, pp 337‑348.

[B65] Ferris, L. P., King, B. G., Spence, P. W., and Williams, H., Effect of Elec​tric Shock on the Heart.  AIEE Transactions, vol 55, May 1936, pp 498 ‑ 515, 1263.

[B66] Ford, G. L., and Geddes, L. A., Transient Ground Potential Rise in Gas​Insulated Substations ‑ Assessment of Shock Hazard.  IEEE Transactians on Apparatus and Systems, vol PAS‑101, no 10, Oct 1982, pp 3620‑3629.

[B67]  Gagnon, J., and Mukhedkar, D., “Earth Resistivity Measurement in a Two-Layer Structure”, IEEE Transactions, Vol. PAS-93, 1974 (We need a copy of this paper)
[B68] Garrett, D. L., Determination of Maximum Ground Fault Current Through Substation Grounding System Considering Effects of Static Wires and Feeder Neutrals, Proceedings of Southeastern Electric Exchange, Atlanta, GA, 1981.

[B69] Garrett, D. L. and Holley, H. J., Calculation of Substation Ground Resistance Using Matrix Techniques.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑99, no 5, Sept/ Oct 1980, pp 2008 ‑ 2011.

[B70] Geddes, L. A., and Baker, L. E., Response to Passage ot Electric Current Through the Body.  Journal of Association for the Advancement of Medical Instruments, vol 2, Feb 1971, pp 13-18.

[B71] Gieiges, K. S., Electric Shock Hazard Analysis.  AIEE Transactions, vol 75, part III, 1956, pp 1329‑1331.

[B72] Graybill, H. W., Koehler, H. C., Nadkarni, J. D., and Nicholas, J. H., Termination of High‑Pressure Oil Cables in Gas‑Insulated Minisubstation Equipment.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑93, no 5, Sept/Oct 1974, pp 1669‑1674.

[B73] Gross, E. T. B., et al.  Grounding Grids for High Voltage Stations.  AIEE Transactions, vol 72, Aug 1953, pp 799‑810.  Not found in guide. 

[B74] Heppe, R. J., Computation of Potential at Surface Above an Energized Grid or Other Electrode, Allowing for Nonuniform Current Distribution.  IEEE Trans​actions on Power Apparatus and Systems, vol PAS‑98, no 6, Nov/Dec 1979, pp 1978 ‑ 1989.

[B75] Heppe, R. J., Step Potentials and Body Currents for Near Grounds in Two​ Layer Earth.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑98, no 1, Jan / Feb 1979, pp 45 ‑ 59.   Not found in guide.
[B76] IEEE Working Group on Electrostatic Effects of Transmission Lines, Gen​eral Systems Subcommittee.  Electrostatic Effects of Overhead Transmission Lines, Part I ‑Hazards and Effects, IEEE Transactions on Power Apparatus and Systems, vol PAS‑91, Mar/Apr 1972, pp 422‑426.

[B77]  IEEE Std 80-1986, (Practical Applications), IEEE Tutorial Course Text 86, EH-253-5-PWR, Chapter 2, (Soil Resistivity Analysis)

[B78]  Jackson, J. D., "Classical Electrodynamics," (book), John Wiley & Sons, Inc. 

[B79] Jones, W. R., Bentonite Rods Assure Ground Rod Installation in Problem Soils. IEEE Transactions on Power Apparatus, vol PAS‑99, no 4, July/Aug 1980, pp 1343‑1346.

[B80] Joy, E. B., Meliopoulos, A. P., and Webb, R. P., Touch and Step Calculations for Substation Groundings Systems.  Paper A-79‑052‑2, presented at IEEE/PES Winter Power Meeting, New York, NY, Feb 1979.

[B81] Kercel, S. W., Design of Switchyard Grounding Systems Using Multiple Grids.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑100, no 3, Mar 1981, pp 1341 ‑1350.

[B82] Kinyon, A. L., Earth Resistivity Measurements for Grounding Grids.  AIEE Transactions, vol 20, Dec 1961, pp 795‑800.

[B83] Kiseiev., Research into Electric Shock. Electrical Review, vol 3l, Dec l965.

[B84] Kouwenhoven, W. B., et al.  AC Shocks of Varying Parameters Affecting the Heart. AIEE Transactions, vol 78, part I, 1959, pp 163 ‑ 169.

[B85] Langer, H., Messungen von Erderspannungen in einem 220 kV Umspanwerk. Electrotechnische Zietschrift, vol 75, no 4, Feb 1954, pp 97‑105 (English translation available in AIEE No. 80‑1961, Appendix V, pp 91 102).

[B86]  Lazzara, J., and Barbeit, N., “Simplified Two-layer Model Substation Ground Grid Design Methodology”, IEEE Transactions, Vol., 5, No. 4, pp 1741-1750, November 1990

[B87] Laurent, P. G., Les Bases Generates de la Technique des Mises a la Terre dans les Installations Electriques.  Bulletin de la Societe' Francaisee des Electriciens, vol 1, ser 7, July 1951, pp 368‑402.
[B88]  Laurent, P. G. "Les Bases Generales de la Technique des Mises a la Terre dans les Installations Electriques". Bulletin de la Societe Francaise des Electriciens, Vol.1, Ser.7, pp 368-402, July, 1951

[B89] Lee, W. R., Death from Electrical Shock.  Proceedings of the IEEE, vol 113, no 1, Jan 1966, pp 144‑148.

[B90] Loucks, W. W., A New Approach to Substation Grounding. Electrical News and Engineering, May 15, 1954.

[B91] Mahonar, V. N., and Nagar, R. P., Design of Steel Earthing Grids in India. IEEE Transactions of Power Apparatus and System, vol PAS‑98, no 6, Nov/Dec 1979, pp 2126 ‑2134.

[B92] Manual on Ground Resistence Testing.  Publication no 25‑J, James G. Bid​dle Co, 1952.

[B93] Meliopoulos, A. P., Papalexopoulos, A., and Webb, R. P., Current Division in Substation Grounding System.  Proceedings of the 1982 Protective Relaying Conference, Georgia Institute of Technology, Atlanta, GA, May 1982.

[B94]  Meliopoulos, A. P. S., Xia, F., Joy, E. B., Cokkinides, G. J., "An Advanced Computer Model for Grounding System Analysis". IEEE Transactions on Power Delivery, Vol.8, pp 13-23, 1993

[B95]  Meliopoulos, A.P., Papelexopoulos, A. D., Webb, R., and Blattner, C. J., “Estimation of Soil Parameters from Driven-Rod Measurements”, IEEE Transactions, Vol. 103, No. 9, September, 1994

[B96] Meliopoulos, A.P., and Papelexopoulos, A. D., “Interpretations of Soil Resistivity Measurement Experience with the Model SOMIP” IEEE Transactions, October, 1986

[B97] Miller, HART, and BROWN.,  Stray Current and Galvanic Corrosion of Rein​forced Steel in Concrete.  Material Performance, vol 15, no 5, May 1976, pp 20 ‑ 27.

[B98] Mitani, H., Magnitude and Frequency of Transient Induced Voltage in Low‑Voltage Control Circuits of Power Stations and Substations.  IEEE Transactions on on Power Apparatus and Systems, vol PAS‑99, no 5, Sept/Oct 1980, pp 1871‑ 1878.   Not found in guide.
[B99]  Moore, R., “An Empirical Method of Interpretation of Earth Resistivity Measurements”, Amercian Institute of Mning Engineering, Column, 164, pp 197-231, 1945 (We need a copy of this paper)
[B100] Morgan, V. T., Rating of Conductors for Short‑Design Currents.  Proceed​ings of the IEEE, vol 118, no 3‑4, Mar/Apr 1971, pp 555 ‑ 570.

[B101] Mukhedkar, D., Gervais, Y., and Dejean, J. P., Modeling a Grounding Electrode. IEEE Transactions on Power Apparatus and System, vol PAS‑92, no 1, Jan 1973, pp 295‑297.

[B102] Mutual Design Considerations for Overhead AC Transmission Lines and Gas Transmission Pipelines.  EPRI Final Report EL‑904, vols 1 and 2, Sept 1978.

[B103] Nahman, J. M., and Salamon, D. D., Analytical Expressions for the Resist​ance of Grounding Grids in Nonuniform Soil.  IEEE Transactions on Power Appa​ratus and Systems, vol PAS‑103, pp 880‑885, Apr 1984.

[B104] Nahman, J.M., and Salamon, D.D.,  Analytical Expressions for the Resist​ance of Rodbeds and of Combined Groundinq System in Noununiform Soil.  IEEE Paper 86 WM126‑7, presented at the IEEE‑PES Winter Meeting, New York, Feb 2 ‑ 7, 1986.

[B105]  Nahman, J. M., and Salamon, D., “A Practical Method for the Interpretation of Earth Resistivity Data Obtained from Driven Rod Tests”,  IEEE Transactions, Vol. 3, No. 4, October, 1988

[B106] Nieman, J., Unstellung von Hochstspannungs‑Erdungsalagen Aufden Be​trieb Mit Starr Geerdetem Sternpunkt.  Electrotechnische Zeitschrift, vol 73, no 10, May 1952, pp 333‑337.

[B107] Nunnally, H. N., Webb, R. P., Joy, E. B., and Meliopoulos, A. P., Com​puter Simulation for Determining Step and Touch Potentials Resulting from Faults or Open Neutrals, in URD Cable.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑98, no 3, May/June 1979, pp 1130‑1136.   Not found in guide.
[B108] Ollendorff, F., Erdstrome (Ground Currents).  Stuttgart, Germany: Springer‑Verlag, 1928; Burkhauser‑Verlag‑Baselund, 1969.

[B109]  Orellara, E., and mooney, H. M., “Two and Three Layer Master Curves and Auxiliary Point Diagrams for Bertical Electrical Sounding Using Wenner Arrangement”,  Interciencia, 1972 Madrid-13, Spain

[B110] Osypka, P., Quantitative Investigation of Current Strength and Routing in AC Electrocution Accident Involving Human Beings and Animals.  Technische Hochschule Braunschweig, Brunswick, West Germany, 1966/SLA Translation Center TT-6611470.

[B111] Palmer, L. S., Examples of Geotechnical Surveys.  Proceedings of the IEE, Paper 2791‑M, vol 106, June 1959, pp 231‑244.

[B112] Patel, S. G., Field Measurements at Texas Valley Substation.  Presented at the Workshop on High Voltage Power System Grounding, Georgia Institute of Technology, Atlanta, GA, May 12‑14, 1982.

[B113]  Purdy, A. B., “Accurate Equations for the Characteristics of Rod Eelctrodes in a Homogeneous Medium”, IEEE PES Winter Meeting, 1979

[B114]  Roman, I., “Some Interpretations of Earth Resistivity Data”, American Institute of Mining and Metallurgical Engineering, Vol. 110, pp. 183-200, 1934

[B115] Rosa, E. B., McCollum, B., and Peters, 0. S., Electrolysis in Concrete. Department of Commerce, Technical Paper of Bureau of Standards, no 18, Mar 1913, pp 1 ‑ 137.

[B116] Rudenberg, R., Distribution of Short‑Circuit Currents in Ground.  Elektro​technische Zeitschrift, vol 31, 1921.    Not found in guide.
[B117] Rudenberg, R., Basic Considerations Concerning Systems.  Etectrotech​nische Zeitschrift, vols 11 and 12, 1926.

[B118] Rudenberg, R., Grounding Principles and Practices‑1, Fundamental Con​siderations on Grounding Currents.  Electrical Engineering, vol 64, no 1, Jan 1945, pp 1 - 13.

[B119] "Safe Substation Grounding, Part l," IEEE Conimittee Report, J. G. Sverak, Chairman, IEEE Transactions on Power Apparatus and Systems, vol PAS‑100, no 9, pp 4281‑4290, Sept 1981.
    Not found in guide.
[B120] "Safe Substation Grounding, Part II," IEEE Committee Report, J. G. Sverak, Chariman, IEEE Transactions on Power Apparatus and Systems, vol PAS‑101, no 10, pp 4006‑4023, Oct 1982.26    Not found in guide.
[B122] Schlichter, “The Interpretation of the Resistivity Prospecting Method for Horizontal Structures”, Physics, Vol. 4, pp 307-322, September, 1933

[B122] Schwarz, S. J., Analytical Expression for Resistance of Grounding Sys​tems.  AIEE Transactions,, vol 73, part III‑B, 1954, pp 1011 ‑ 1016.

[B123] Sebo, S. A. Zero Sequence Current Distribution Along Transmission Lines. IEEE Transactions on Power Apparatus and Systems, vol PAS‑88, June 1969, pp 910‑919.

[B124] Semlyen, A., Ground Return Parameters of Transmission Lines as Asymp​totic Analysis tor Very High Frequencies.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑100, no 3, Mar 1981 pp 1031‑ 1038.

[B125] Smith, G. E., Resistivity of Some Surface Coverings Used in Substation Yards as a Function of Resistivity of the Wetting Agent and as a Function of Time After Wetting. Internal Report of Carolina Power and Light Co, Apr 20, 1978.   Not found in guide.
[B126] Stauffacher, E. R., Short Time Current Carrying Capacity of Copper Wire.  General Electric Review, vol 31, no 6, June 1928, pp 326‑327.Not found in guide.
[B127] Substation Grounding Scale Model Tests.  EPRI Interim Report EL‑3099, May 1983.

[B128] Sunde, E. D., Earth Conduction Effects in Transmission Systems.  New York: McMillan, 1968.

[B129] Sunde, E. D., "Earth Conduction Effects in Transmission Systems". (book), Dover Publications, Inc., New York, 1968.

[B130] Sverak, J. G., Optimized Grounding Grid Design Using Variable Spacing Technique. IEEE Transactions on Power Apparatus and Systems, vol PAS‑95, no 1, Jan/Feb 1976, pp 362‑374.   Not found in guide.
[B131] Sverak, J. G., Simplified Analysis of Electrical Gradients Above a Ground Grid; Part I ‑ How Good is the Present IEEE Method? IEEE Transactions on Power Apparatus and Systems, vol PAS‑103, no 1, Jan 1984, pp 7‑25.

[B132] Sverak, J. G., Sizing of Ground Conductors Against Fusing.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑ 100, no 1, Jan 1981, pp 51 ‑ 59.

[B133] Sverak, J. G., Booraem, C. H., and Kasten, D. G., Post‑Design Analysis and Scale Model Tests for a Two Grid Earthing System Serving the 345 kV GIS Facilities at Seabrook Power Plant.  Paper 410‑06, Proceedings of the CIGRE Sym​posium on High Currents in Power Systems Under Normal, Emergency and Fault Conditions, Brussels, , June 3‑5 1985.

[B134] Tagg, G. F., Earth Resistances.  New York: Pitman, 1964.    Not found in guide.
[B135]  Tagg, G. F., Interpretation of Resistivity Measurements”, American Institute of Mining and Metallurgical Engineering Transactions, Vol. 110, pp135-147, 1934

[B136]  Takahashi, T., and Kawase, T., “Analysis of Apparent Tesistivity in Multi-Layer Earth Structure” IEEE Transactions, Vol. 5, No. 2, April, 1990

[B137] Taylor, H. G., The Earth‑Loading Capacity of Earth Electrodes.  IEE Journal, vol 77, Oct 1935, p 542.  Not found in guide.
[B138] Thapar, B., and Gross, E. T. B., Grounding Grids for High Voltage Sta​tions ‑ Part IV‑Resistance of Grounding Grids in Nonuniform Soil.  IEEE Tran​sactions on Power Apparatus and Systems, vol PAS‑82, Oct 1963, pp 782 ‑ 788.

[B139]  Thapar, B., Gerez, V., Singh, V., "Effective Ground Resistance of the Human Feet in High Voltage Switchyards". IEEE Transactions on Power Delivery, Vol.8, pp 7-12, 1993

[B140]  Thapar, B., Gerez, V., Emmanuel, P., "Ground Resistance of the Foot in Substation Yards". IEEE Transactions on Power Delivery, Vol.8, pp 1-6, 1993

[B141]  Thapar, B., Gerez, V., Kejriwal, H., "Reduction Factor for the Ground Resistance of the Foot in Substation Yards". IEEE/PES 1993 Winter Meeting, Paper # 93WM 121-4-PWRD.

[B142] Thapar, B., and Gross, E. T. B., “Grounding Grids for High Voltage Stations”, IEEE Transactions on PAS, October, 1963

[B143] Towne, H. M., Lightning Arrester Grounds ‑ Parts I, II, and III.  General Electric Review, vol 35, Mar ‑ May, 1932, pp 173 ‑ 280.

[B144]  Ufermann, J., and Jahn, K., “High Frequency Earth Resistance Measuring Instrument, Brown and Boverie Journal, No. 3/67, pp 132-135

[B145] Use of Aluminum for Substation Buses.  Working Group 57.1. IEEE Paper 62-280.  Not found in guide.
[B146] Verma, R., Merand, A., and Barbeau, P., Design of Low Resistence Grounding System for Hydro‑Electric Plant Located on Highly Resistive Soils.  IEEE Transactions of Power Apparatus and Systems, vol PAS‑97, no 5, Sept/Oct 1978, pp 1760‑1768.

[B147] Verma, R., and Mukhedkar, D., Ground Fault Current Distribution in Substation, Towers and Ground Wire.  IEEE Transactions on Power Apparatus and Systems, vol PAS‑98, May/,June 1979, pp 724 ‑ 730.

[B148]  Wenner, F., A Method of Measuring Earth Resistances.  Bulletin of the Bureau of Standards, Rep no 258, vol 12, no 3, Feb 1916, pp 469‑482.

[B149] Yu, L., Determination of Induced Currents and Voltages in Earth Wires During Faults.  Proc.  IEE, vol 120, no 6, June 1973, pp 689‑692.  Not found in guide.
[B150] Zaborszky, J., Efficiency of Grounding Grids with Nonuniform Soil. AIEE Transactions, vol 74, Dec 1955, pp 1230 ‑ 1233.  Not found in guide.

Moved from References

ASTM D448-80, Specifications for Standard Sizes of Coarse Aggregate for High Construction (ANSI).

IEEE C37.010-1979, IEEE Application Guide for AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis (ANSI).

Annex  B

Sample calculations

(Informative)

This annex illustrates the application of equations, tables, and graphs for designing a substation grounding system.  The specific objectives are as follows:


(1) To show the application of principal equations of the guide for several refinements of the design concept toward a satisfactory final design solution


(2) To illustrate the typical differences to be expected between results obtained using the simplified calculations of this guide and the more rigorous computer solutions.


(3) To illustrate such design conditions for which the use of simplified calculations of this guide would not be appropriate for a safe design, as some of the equations may only be used with caution.

In view of these objectives, the following series of examples B1‑B5 neither represents, nor is intended to be, the best or most efficient way to design a grounding system.

The SGA package of computer-based grounding programs, described in EPRI's Final Report EL ‑ 2682, Vol. 2, was used to model the grids in these examples.[B??   ]  This is not intended as an endorsement, and there is no claim made as to the accuracy or validity of these programs.

For the series of examples B1‑B3, the design data are as follows:


Fault duration tf
= 0.5 s


Fault impedance Z1
= 4.0 + j10.0 (

Fault impedance Z0
= 10.0 + j40.0 (

Current division factor Sf
= 0.6


Line‑to‑line voltage at worst‑fault location
= 115,000 V


Soil resistivity (
= 400 (‑m


Crushed rock resistivity (wet) (s
= 2500 (‑m


Thickness of crushed rock surfacing hs
= 0.1 m (4 in)


Depth of grid burial h
= 0.5 m


Available grounding area A
= 63 m ( 84 m

The crushed rock resistivity is assumed to be a conservative estimate based on actual measurements of typical rock samples.  The fault impedances and current division factor Sf are determined for the worst‑fault type and location, including any conceivable system additions over the next 25 years.  Thus, no additional safety factor for system growth is added.  In addition, it is assumed that the substation will not be cleared by circuit breakers with an automatic reclosuring scheme.  Thus, the fault duration and shock duration are equal.

B1. Square grid without ground rods ‑ example 1
Using the step‑by‑step procedure as described in 16.4 and illustrated in figure 16-1, the following design evaluations can be made.

Step 1: Field data.  Although the substation grounding grid is to be located within a rectangle of 63 m ( 84 m (5292 m2), for the initial design assessment it may be expedient to assume a square 70 m ( 70 m grid with no ground rods.  Consequently, the area occupied by such a grid is A = 4900 m2.  An average soil resistivity of 400 (‑m is assumed, based on soil resistivity measurements.

Step 2: Conductor size.  Ignoring the station resistance, the symmetrical ground fault current If ( 3I0, is computed using equation (65):




(B1)




(B2)

and, hence  (3I0( = 3180 A

Because the fault duration is 0.5 s, according to table 15.1 of Clause 15.10 the decrement factor Df is 1.00; thus, the rms asymmetrical fault current is also 3180 A.  For a conservative design, this current magnitude will be used to determine the minimum diameter of ground conductors.

Assuming the use of copper wires and ambient temperature of 40(C, the simplified equation (41) and table 11.2 of Clause 11 is used to obtain the required conductor cross‑sectional area.  For 0.5 s and using the melting temperature of 1084 (C for hard‑drawn copper, the required cross-sectional area in circular mils is




(B3)




(B4)

Because Ac = (d2/4 the conductor diameter is less than 3.5 mm, or 0.0035 m.

Based on this computation, a copper wire as small as size AWG No 8 could eventually be used, but due to the mechanical strength and ruggedness requirements, a larger (2/0 AWG) conductor with diameter d = 0.0105 m (0.414 in) is usually preferred as a minimum.

Consequently, at this stage, the designer may opt to check if, alternately, the use of a less conductive (30%) copper‑clad steel wire and the imposition of a more conservative maximum temperature limit of 700 (C will still permit the use of a conductor with diameter d = 0.01 m.

Using equation (40) and table 11.1 of Clause 11.3 gives




(B5)




(B6)

In this case, dmin = 4.46 mm, or approximately 0.005 m, which is less than d = 0.01 m desired.  Hence, a 30% copper‑clad steel wire of AWG 2/0 size is a viable alternative for grid wires, even if a conservative maximum temperature limit of 700(C is imposed.

Step 3: Touch and step criteria.  For a 0.102 m (4 in) layer of crushed rock surfacing, with resistivity of 2500 (‑m, and for an earth with resistivity of 400 (-m, the reflection factor K is computed using equation (23) of Clause 7.4:





(B7)




(B8)

Figure 7.6 of Clause 7.4 indicates for K = -0.72 the resistivity of crushed rock is to be derated by a reduction factor C ( 0.74.  The reduction factor C can also be approximated using equation (28) of Clause 7.4:




(B9)




(B10)

Assuming that for the particular station the location of grounded facilities within the fenced property
 is such that the person's weight can be expected to be at least 70 kg, equations (30b) and (32b) may be used to compute the tolerable step and touch voltages, respectively, as follows:

Estep70 =


(B11)




(B12)

Etouch70 = 


(B13)




(B14)

Step 4: Initial design.  Assume a preliminary layout of 70 m (70 m grid with equally spaced conductors, as shown in figure B1, with spacing D = 7 m, grid burial depth h = 0.5 m, and no ground rods.  The total length of buried conductor, L, is 2 ( 11 ( 70 m = 1540 m.

Fig B1
Square grid without ground rods
Step 5: Determination of grid resistance.  Using equation (50) of Clause 14.2, for L = 1540 m, and grid area A = 4900 m2 the resistance is




(B15)




(B16)

Step 6: Maximum grid current IG. Per procedure and definitions of 15.1, the maximum grid current IG is determined by combining equations (61) and (62) of Clause 15.1.  Referring to Step 2, for Df = 1.0, and the given current division factor Sf = 0.6,




(B17)

and



(B18)

Thus,




(B19)




(B20)

Step 7: Now it is necessary to compare the product of IG and Rg, or GPR, to the tolerable touch voltage, Etouch70.



 volts
(B21)

which far exceeds 838 V, determined in Step 3 as the safe value of Etouch7O.  Therefore, further design evaluations are necessary.

Step 8: Mesh voltage.  Using equation (76) of Clause 16.5, Km is computed:




(B22)




(B23)

where




 





and









The factor Ki is computed using equation (78):



(B24)




(B25)

where





















and





Finally, Em is computed using eq. 75 and 79:




(B26)




(B27)

Step 9: Because the estimated mesh voltage is higher than the tolerable touch voltage (that is, 1002.1 V versus 838.2 V), the grid design must be modified.

For comparison, the SGA programs result in 2.67 ohms, 984.3 V and 498.7 V for the grid resistance, touch voltage and step voltage, respectively, for this example.

B2.
Square grid with ground rods ‑ example 2 

In the previous example B1, Step 10 of the design procedure has not been reached due to the failure to meet the criterion of Step 9. Generally, there are two approaches to modifying the grid design to meet the tolerable touch voltage requirements: (1) reduce the GPR to a value below the tolerable touch voltage or to a value low enough to result in a value of Em below the tolerable touch voltage, and (2) reduce the available ground fault current.   Usually, (2) is difficult or impractical to achieve, so the grid is modified by changing any or all of the following: grid conductor spacing, total conductor length, grid depth, addition of ground rods, etc.  In this example, the preliminary design will be modified to include 20 ground rods, each 7.5 m (24.6 ft) long, around the perimeter of the grid, as shown in figure B2, below.

Fig B2 
Square grid with twenty 7.5 m rods
Step 5. Using equation (50) of Clause 14.2, for L = 1540 + 20(7.5 = 1690 m, and A = 4900 m2 yields the following value of grid resistance Rg: 




(B28)




(B29)

Steps 6 and 7. The revised GPR is (1908)(2.75) = 5247 V, which is still much greater than 838.2 V.

Step 8. Using equation (76) of Clause 16.5, Km is computed:




(B30)




(B31)

where





and









This time, Em is computed using Eq. 75 and 79:




(B32)




(B33)

Step 9. Now the calculated corner mesh voltage is lower than the tolerable touch voltage (747.4 V versus 838.2 V), and we are ready to proceed to step 10.

Step 10: Step voltage criterion.  Because the step voltage has not been calculated yet, equations (78), (81) and (82) are used to compute Ki, Es, and Ks, respectively.  Note that the value for Ki is still 1.272 (same as for mesh voltage).




(B34)




(B35)

Then




(B36)




(B37)

Step 11.  The computed Es is well below the tolerable step voltage determined in Step 3 of example 1.  That is, 548.9 V is much less than 2686.6 V.

Step 12 .  A safe design has been obtained.  At this point, all equipment pigtails, additional ground rods for surge arresters, etc., should be added to complete the grid design details.

For comparison, the SGA programs result in 2.52 ohms, 756.2 V and 459.1 V for the grid resistance, touch voltage and step voltage, respectively, for this example.

B3.
Rectangular grid with ground rods ‑ example 3 
In this example the preliminary grid design will be reconciled in terms of the actual shape of the grounding area as an alternative design.  Realizing that the full grounding area is only about 8% larger than that used in the previous calculations, most of the conclusions from example 2 can be used for arriving at a suitable final design solution.

Choosing, again, spacing D = 7 m, for a rectangular 63 m ( 84 m grid, the grid wire pattern is 10 ( 13, and the grid conductor combined length is 13 ( 63 m + 10 ( 84 m = 1659 m.  Assume the use of 38 ground rods, each 10 m long, as shown in figure B3.

Step 5. Again, using equation (50) of Clause 14.2, but for L = 1659 m + (38)(10 m) = 2039 m and A = 63 m ( 84 m = 5292 m2, gives




(B38)




(B39)

Steps 6 and 7. Using IG = 1908 A as before, and RG = 2.62 ohms, the GPR = (1908)(2.62) = 4998.96V, which is much greater than 838.2 V.

Fig B3
Rectangular grid with thirty‑eight 10 m ground rods
Step 8. For the particular design arrangement shown in Fig B3, eq. 75, 76,77 and 79 can again be used to estimate the corner mesh voltage.  However, since the grid is rectangular, the value of n to be used in the mesh voltage computation will be different, based on the factors below.



























Now Km is computed using equation (77) of Clause 16.5:




(B40)




(B41)

where









Equation (77) is used to compute Ki :




(B42)




(B43)

Finally, Em is computed using Eq. 75 and 79:



 
(80)



 
(B81)

Step 9: Touch voltage criterion. This calculated mesh voltage is  well below the Etouch7O limit of 838.2, but uses 119 m of additional conductor and 230 m of additional ground rods, as compared with the previous example.  Thus, the mesh spacing could be reduced, the number and/or length of ground rods could be reduced, or both to achieve the same margin of safety as example B2.

The remaining steps are the same as demonstrated above and will not be repeated here.

For comparison, the SGA programs result in 2.28 ohms, 519.4 V and 349.7 V for the grid resistance, touch voltage and step voltage, respectively, for this example.

B4.
Equally spaced grid with ground rods in two‑layer soil ‑ Exhibit 1
The SGA package of grounding computer programs, described in EPRI's Final Report EL ‑ 2682, Vol. 2, was used to model an equally spaced grid in two‑layer soil.

Fig B4 
Equally spaced square grid with nine rods in two‑layer soil
Fig B5
Diagonal voltage profile for the grid of fig B4 in two‑layer soil
As shown in figure B4, the 61 m ( 61 m (200 ft ( 200 ft) grid consisted of four meshes per side, and had nine ground rods, each 9.144 m (30 ft) long.  The diameter of ground rods was 0.0127 m (0.5 in).  The grid consisted of four meshes per side, formed by wires of a 0.01 m diameter, buried 0.5 m below the earth's surface.  The depth of the upper layer 300 (‑m soil was 4.47 m (15 ft); the lower soil had resistivity of 100 ohm/m.

The computer‑calculated values of resistance, corner mesh voltage, and maximum step voltage, were as follows:

Rg = 1.353 ohms
Em = 49.66% of GPR
Es = 18.33% of GPR

As can be determined from figure B5, the mesh voltage coordinates were X = ‑75.00 ft, and Y= ‑75.00 ft, that is, near the center of the corner mesh.  The maximum step voltage (not shown) was calculated outside the grid, between the grid corner (X, Y = ‑100 ft) and the point at X, Y = 102.12 ft, that is, approximately over 1 m distance in a diagonal direction away from the grid corner.

Fig B6

Unequally spaced square grid with twenty-five 9.144 m rods
B5.
Unequally spaced grid with ground rods in uniform soil ‑ Exhibit 2
The SGA package was also used to model a square grid with unequally spaced conductors, shown in figure B6.

The computer output included the grid resistance, a surface voltage profile, the step voltage because of a more dense spacing between the peripheral conductors, and the corner mesh voltage.

As shown in Fig B7, the corner mesh voltage is only 9.29% of the GPR, while the maximum touch voltage, occurring above the largest interior mesh, is 17.08% of the GPR.

The maximum touch voltage, thus, did not occur in the corner mesh.  For other choices of conductor spacings, the maximum touch voltage may occur above some other meshes.  Therefore, for unequal spacings, the touch voltages must be investigated over the entire grid, and the simplified criterion for checking the corner mesh voltage alone is not sufficient.  On the other hand, the resistance Rg is not too dependent on the exact configuration of grid conductors and ground rods. (For instance, were Rg estimated by equation (50) for a combined length of grid conductors and ground rods L = 18 ( 19.44 m + 25 ( 9.144 m = 1874.5 m, the calculated value of 1.61 ( would be less than 14% higher than the value of 1.416 ( calculated by the computer.)

Fig B7
Diagonal voltage profile for an unequally spaced grid of Fig B6
Annex  C

Graphical and approximate analysis of current division 

(Informative)

C1.  Introduction

A graphical method for determining the maximum grid current, based on results obtained using the SMECC program has been developed. This method attempts to correlate the substation zero sequence fault obtained from a standard short circuit study to the actual current flowing between the grounding system and surrounding earth. The original presentation of this concept was published in /1/. That paper describes the parametric analysis performed and  the resulting basis for the assumptions used to develop the curves. Additional curves have since been developed to address other system configurations. The following is an explanation of the use of the graphs shown in figures C1 through C22.
The graphs are divided into four categories:

a) 100% remote and 0% local fault current contribution, representing typical distribution substations with delta-wye transformer, with X transmission lines and Y feeders (figures C1 through C16)

b) 50% remote and 50% local fault current contribution (figures C17 and C18)

c) 75% remote and 25% local fault current contribution (figures C19 and C20)

d) 25% remote and 75% local fault current contribution (figures C21 and C22)

Categories (2), (3), and (4) represent typical transmission substations or generating plants with X transmission lines(feeders are considered to be transmission lines in these cases), and with local sources of zero sequence current, such as auto transformers, three winding transformers, generators(grounded-wye GSU's), etc.

The following assumptions were used to obtain the graphs:

1) Transmission line length of 23.5 miles and a distance between grounds of 0.0947 miles (500 feet).

2) Transmission tower footing resistance of 15 or 100 .

3) Transmission line structure single pole with 1- 7#10 alumoweld shield wire and 336.4 kcmil, 26/7 acsr conductor.

4) Distribution line length of 2.5 miles and a distance between grounds of 0.0758 miles (400 feet).

5) Distribution pole footing resistance 25 or 200 .

6) Distribution pole  3 phase triangular layout, with one 336.4 kcmil, 26/7 acsr phase and 1/0 acsr neutral conductor.

7) Soil resistivity of 100 -meters.

8) Substation resistances of 0.1, 0.5, 1.0, 5.0, 10.0, and 25.0 .

9) Number of transmission lines varied from 1, 2, 4, 8, 12, and 16.

10) Number of distribution lines varied from 0, 1, 2, 4, 8, 12, and 16. 

11) One remote source for each two(2) transmission lines.

C2  How to use the graphs and equivalent impedance table

On each graph, a family of curves is plotted, with each curve representing a different number of transmission lines and/or feeders. The abscissa  is a range of grounding system impedances from 0.1 to 25.0 ohms. The ordinate is the percent of the total zero sequence substation bus ground fault which flows between the grounding system and surrounding earth.

Table C1 shows the system impedance at 1 .  The magnitude of the equivalent total ground impedance is 
.  From table C1, the equivalent impedance of the line and feeders is 0.54 +j 0.33 , and a feeder footing resistance of 25 , a total fault current of 1600 amperes, transmission footing resistance of 15 . To determine the GPR with current splits, parallel the grid resistance with the appropriate impedance from the table and multiply this value by the total fault current. For example, a substation with 1 transmission line and 2 feeders has a resistance of 5  and feeder pole ground  resistance of 200 .  The second column of impedances is for transmission footing resistance of 100  and feeder pole ground resistance of 25  for 100% remote contribution with X transmission lines and Y feeders.  The first column of impedances is for transmission line tower footing resistance of 15 



 
and the GPR is




 volts

To calculate the grid current, divide the GPR by the resistance.




 Amperes

The grid current may also be computed directly by current division.




 amperes

C3  Examples

To illustrate the use of the graphical analysis, consider the example shown in figure 23.  The SMECC program calculated the maximum grid current of 2,354.6 amperes, with a total bus ground fault of 9,148.7 amperes.  The system in question had two transmission lines with a tower footing resistance of 15.0 .  Figure C4 shows curves for two lines/ two feeders and two lines/ four feeders.  Thus, interpolation was necessary for this example.  From figure C4, we see that the approximate split factor Sf was (32+23)/2 or 27.5%. The maximum grid current was
 and a feeder pole resistance of 25.0 



 Amperes

Using table C1, the equivalent impedance of the system neutral circuit for two lines and two feeders is 0.455 + j0.241 .  The average of the split factors for these two cases will be used.
, and for two lines and four feeders is 0.27 + j0.165 




Thus, Sf = (0.349 +0.247) / 2 = 0.298 or 29.8%

The resulting grid current using this method is




 Amperes

Both methods compare favorably with the value of 2,354.6 amperes or 26% of 3I0 from the program SMECC, though the equivalent impedance method is generally more conservative.

Next consider the more complex system shown in figure C24.  This example is similar to the first, except that the distribution substation is replaced with a local source of generation, such as a cogeneration plant.  For this example, there is both local and remote sources of fault current, so the percent of local vs. remote must be computed.  The SMECC program computed a total fault current of 19,269.6 Amperes at the 115kV bus, with 48.7% contributed by the local source and 51.3% contributed by the remote sources.  The closest curves are for 50/50 split (figure C17).  For a grid resistance of 0.9 ohms, the split factor is determined from the curve for two lines and no feeders - Sf = 29%.  The maximum grid current is




 Amperes

This does not compare as well as the case with 100% remote contribution, but is still better than using the total fault current, or even the remote or local contribution.  For this case, the SMECC program results in a value of 4,034.8 amperes, or 21% of 3I0.  The equivalent impedance method does not work as well for cases other than 100 percent remote contribution, and is not recommended.

C4  Equations for computing line impedances

The following equations are found in the Westinghouse T&D Reference Book, Fourth Edition.[B??   ]  The definitions of the terms used in the equations are:

GMD
is the geometric mean distance between the phase conductors

GMR
is the geometric mean radius of the conductor

dab
=
is the distance between conductors a and b

rc
=
is the ac resistance of the conductor, at frequency f
xa
=
is the inductive reactance of the conductor to one foot spacing, at frequency f

f
=
is the frequency in Hz

De
=
is the equivalent depth of earth return

The positive sequence impedance, Z1, of a transmission line (with earth return), ignoring the effects of overhead static wires, is




  /mile
(C1)

where





The zero sequence self impedance, Z0(a) , of the transmission line (with earth return), with no overhead static wires is




  /mile
(C2)

where





and ra, xa and xd areas defined above using characteristics of the phase conductors.

The zero sequence self impedance, Z0(g) , of one overhead static wire (with earth return) is




  /mile
(C3)

where ra and xa are as defined above using characteristics of the overhead static wire, and re and xe are as defined above.

The zero sequence self impedance, Z0(g) , of two overhead ground wires (with earth return) is




  /mile
(C4)

where





dxy is the distance between the two overhead static wires, ra and xa are as defined above using characteristics of the overhead static wire, and re and xe are as defined above.

The zero sequence mutual impedance, Z0(ag) between one circuit and n ground wires (with earth return) is




  /mile
(C5)

where





dag1 is the distance between phase a and the first overhead static wire, etc., and re and xe are as defined above.

Then, the zero sequence impedance of one circuit with n ground wires (and earth return) is




  /mile
(C6)

These equations for Z1 and Z0 are used, along with appropriate impedances for transformers, generators, etc., to compute the equivalent fault impedance.

To compute the impedance of an overhead static wire or feeder neutral for use in Endrenyi's formula, the simple self impedance (with earth return) of the conductor is used.




  /mile
(C7)

where

ra and xa are as defined above using characteristics of the overhead static wire or feeder neutral, and re and xe are as defined above.

Table C1.

Approximate equivalent impedances of

transmission line overhead static wires and feeder neutrals

NUMBER

OF

TRANSMISSION

LINES
NUMBER

OF

FEEDER

NEUTRALS
LINE RTFR = 15

LINE RTFR = 25

R + jX ()
LINE RTFR = 100

LINE RTFR = 200

R + jX ()

1
1
0.91 + j.485
3.27 + j.652

1
2
0.54 + j0.33
2.18 + j.412

1
4
.295 + j0.20
1.32 + j.244

1
8
0.15 + j0.11
.732 + j.133

1
12
0.10 + j.076
.507 + j.091

1
16
.079 + j.057
.387 + j.069

2
1
.685 + j.302
2.18 + j.442

2
2
.455 + j.241
1.63 + j.324

2
4
0.27 + j.165
1.09 + j.208

2
8
0.15 + j0.10
.685 + j.122

2
12
0.10 + j0.07
0.47 + j.087

2
16
0.08 + j.055
.366 + j.067

4
1
0.45 + j0.16
1.30 + j.273

4
2
0.34 + j0.15
1.09 + j 0.22

4
4
0.23 + j0.12
.817 + j0.16

4
8
.134 + j.083
.546 + j.103

4
12
.095 + j.061
0.41 + j.077

4
16
.073 + j0.05
.329 + j0.06

8
1
0.27 + j0.08
0.72 + j.152

8
2
0.23 + j0.08
0.65 + j.134

8
4
0.17 + j.076
.543 + j0.11

8
8
.114 + j.061
.408 + j.079

8
12
.085 + j.049
.327 + j.064

8
16
.067 + j.041
.273 + j.052

12
1
.191 + j.054
.498 + j.106

12
2
0.17 + j.055
.462 + j.097

12
4
0.14 + j.053
.406 + j.083

12
8
.098 + j.047
.326 + j.066

12
12
.077 + j.041
.272 + j.053

12
16
.062 + j.035
.234 + j.046

16
1
.148 + j0.04
.380 + j.082

16
2
.135 + j.041
.360 + j.076

16
4
.113 + j.041
.325 + j.067

16
8
.086 + j.038
.272 + j.055

16
12
.068 + j.034
.233 + j.047

16
16
.057 + j0.03
.203 + j.040

1
0
2.64 + j0.60
6.44 + j1.37

2
0
1.30 + j0.29
3.23 + j0.70

4
0
.65 + j.15
1.61 + j.348

8
0
.327 + j.074
.808 + j.175

12
0
0.22 + j.049
.539 + j.117

16
0
.163 + j.037
.403 + j.087

0
1
1.29 + j.967
6.57 + j1.17

0
2
.643 + j.484
3.29 + j0.58

0
4
.322 + j.242
1.65 + j.291

0
8
.161 + j.121
.826 + j.148

0
12
.108 + j.081
.549 + j.099

0
16
.080 + j.061
.412 + j.074

Annex  D

Simplified step and mesh equations

(Informative)
In the previous editions of this guide, the following equation was provided for determining the value of a mesh voltage (in volts) on the earth's surface above the center of a corner mesh ‑ assuming an equally spaced rectangular grid, which is buried in depth h in a homogeneous soil of uniform resistivity.  This grid may consist of n parallel conductors spaced D apart, and of an undetermined number of cross connections.  All grid wires are assumed to be of diameter d. The spacing of parallel conductors D, as well as d and h, are in meters.





(D1)

where

-m

is the average soil resistivity in 
I
is the maximum rms current flowing between ground grid and earth

L
is the 
total length of buried conductors, including cross connections, and (optionally) the combined length of ground rods in m

Ki
is the corrective factor for current irregularity

Km
is the mesh factor defined for n parallel conductors,

Reference [B1] derived the factors Km and Ki to account for the geometry of the grounding system.  Sverak [B131] modified the factor, and added the factors Kii and Khin an attempt to improve the accuracy of the results.  The relationship between Km and Em depends largely on the current density in the perimeter conductors versus the current density in the inner conductor.  To reflect this effect of current density and to correct some of the deficiencies in the equation for Km, Sverak added the weighing terms, Kii and Kh into the equation for Km.  The resulting equation for Km was more accurate and versatile than previous forms of the equation:





(D2)

where

Kii
is 1 for grids with ground rods along the perimeter, or for grids with ground rods in the grid corners, as well as both along the perimeter and throughout the grid area,

or, for grids with no ground rods or grids with only a few ground rods, none located in the corners or on the perimeter.




(D3)




(D4)

ho
is 1 m (reference depth of grid)

Because of assumptions made in the derivation of Km, a corrective factor Ki is needed to compensate for the fact that the subject mathematical model of n parallel conductors cannot fully account for the effects of a grid geometry; that is, for two sets of parallel conductors that are perpendicular to each other and interconnected at the cross connection points. For a large number of square and rectangular grids, the mesh voltage was obtained using a computer.  From this computer generated data, a new expression for Ki was found to better fit in the mesh voltage equation. [B??] (Reference Baldev Thapar, "Simplified Equations for Mesh and Step Voltages in an AC Substation," IEEE Transactions on Power Delivery, vol 6, no 2, April 1991.)  This factor is:





(D5)

I  The simplified Em equation used in the previous edition of the guide has been limited to square and rectangular grids with square meshes.  In practice, a large number of grounding grids have shapes other than square or rectangular.  While the specific formula for Km has remained the same as the 1986 edition of the guide, a new value of n based on the geometry of the grid and the geometry of the meshes was developed in [B?? Thapar] to allow the equations to be effective for a variety of grid shapes, including symmetrical T-shaped, triangular, and L-shaped grids.





(D6)

where





Lc
is the total length of the conductor in the horizontal grid, m

Lp
is the peripheral length of the grid, m

A
is the area of the grid, m2
Lx
is the maximum length of the grid in the x direction, m

Ly
is the maximum length of the grid in the y direction, m

Dm
is the maximum distance between any two points on the grid, m

While these changes to the equations did expand their use to include a variety of practical ground grid shapes, they did not include the use of ground rods.  An attempt was made to expand these equation to include the use of ground rods.  If LC represents the total grid conductor length, LR represents the total length of all ground rods, and Rl represents the average length of each ground rod, then for grids with ground rods in the corners, as well as along the perimeter and throughout the grid.





(D7)

The multiplier for LR is an empirical function that reflects the fact that the current density is higher in the ground rods than in the horizontal grid conductors for uniform soil.

In the previous editions of this guide, the following equation was provided for determining the value of the worst case step voltage (in volts)





(D8)

where

-m

is the average soil resistivity in 
I
is the maximum rms current flowing between ground grid and earth

L
is the total length of buried conductors, including cross connections, and (optionally) the total effective length of ground rods in m

Ki
is the corrective factor for current irregularity

Ks
is the mesh factor defined for n parallel conductors,

Sverak has derived a factor Ks, based on the geometry of a ground grid with no ground rods. [B??] (reference Sverak paper).  As with the mesh voltage, this Ks is proportional to the step voltage Es.  Again, computer simulations were used to derive empirical factors to improve the accuracy of previous versions of Es. [B??] (Thapar)




(D9)

where n, D and h are defined above.

While these changes to the equations did expand their use to include a variety of practical ground grid shapes, they did not include the use of ground rods.  An attempt was made to expand these equation to include the use of ground rods.  If LC represents the total grid conductor length and LR represents the total length of all ground rods, then for grids with or without ground rods,





(D10)

These new simplified equations were compared to computer solutions for hundreds of different ground grids and the results were similar to those calculated by the more rigorous computer programs in most cases.

Annex  E

Equivalent uniform soil model for non-uniform soils

(Informative)

In the interest of simplicity, several assumptions have been made in developing the ground grid design equations of this guide.  One such assumption is that these equations accept only a uniform soil resistivity model regardless of the soil under consideration.  The survey, done among the guide users, indicated the need to provide a guideline for representing a soil regardless of its type by a uniform equivalent and, thus, remove this limitation in the use of the design equations.

A typical soil has several layers, each having a different resistivity.  Most often lateral changes also occur, but in comparison to the vertical layers, these changes usually are more gradual.  Station sites where the soil may posses uniform resistivity throughout the area and to a considerable depth are seldom found.  A uniform soil interpretation of apparent resistivities obtained in the field, under these circumstances, is the most difficult  task to perform even with the help of computers.  Accordingly, it must be recognized that the soil model is only an approximation of the actual soil conditions and that a perfect match is unlikely.  However, it has been recognized that the two layer representation of a soil is closer to the actual soil conditions compared to its uniform equivalent.

Sometimes, in a multi-layer soil, the variation in apparent  soil resistivity a with respect to depth or pin spacing is not too great.  Such a soil can be represented as a uniform soil with a single soil resistivity value.  Although it is difficult to draw a clear line to indicate whether the soil is uniform or not, the approach taken by the task force consisted of defining the uniform soil based on the two layer equivalents of several field measured resistivity profiles.  EPRI's SOMIP program was employed to compute two layer equivalents of these soils.  The guideline, evolved as a result of this approach, says that a soil can be represented as a uniform soil if the difference between two extreme values of apparent resistivity is less than 30 percent of the larger resistivity value.  Once the soil is determined to be a uniform soil, the average apparent resistivity value computed from equation (E1), then represents that soil in the design equations.




(E1)

Where -m.
a(n) are the apparent resistivity measurements obtained at n different spacing in four-pin method or at n different depths in driven ground rod method in a(3) --- a(2), a(1), 
A majority of the soils will not meet the above criteria for the uniform soil.  To determine uniform soil models to represent non-uniform soils, the task force took the similar approach.  The measured apparent resistivity data from several sites were interpreted by three different soil models.  Each soil was interpreted by the two-layer soil model computed with the SOMIP program and two different uniform soil models: one determined from equation (E1), and the other determined from equation (E2).




(E2)

Where

-m.
a(max)
is the maximum apparent resistivity value (from measured data), 
-m.
a(max)
is the minimum apparent resistivity value (from measured data), 

The next step was to compute the ground grid resistance Rg, the corner mesh voltage Emesh, and the corner step voltage Estep  for a typical ground grid using EPRI's SGSYS program.  A 250'X250' ground grid with 64 meshes and uniformly distributed ground rods was selected for this investigation.  The length of the ground rods, modeled in SGSYS, varied from one soil case to another.  For a given soil case, this length was determined so as to reach the depths (or pin spacings) where a(av2) occur in the measured apparent resistivity profile.  Figure-E1 illustrates the modeled ground grid including the locations for computed step and touch voltages.
a(av1) and 
Figure-E1   The ground grid modeled in SGSYS for computing grounding parameters

Following the computations, the grounding parameters computed with the two layer model were compared with those computed using the uniform soil models. This comparison indicated that the mesh and step voltages computed with the soil model represented by a(av2) yielded conservative values compared to those computed with the two layer soil model for a majority of investigated soils.

Table E1 presents the comparison of grounding parameters computed using the two layer soil model with those computed using the uniform soil model represented by a(av2) for two typical soils.  These soil types including their apparent resistivity profiles are the same ???as shown in Annex??-    (Annex on Benchmark Cases) and are shown in table-E2 and table-E3 in this Annex.

Table-E1  Ground parameters computed with two layer soil compared with those computed with equivalent uniform soil model

Soil Type
Computed Grounding Parameters with Two Layer Soil Model



Computed Grounding Parameters with Uniform Soil Model





2, h1, 
-m,ft.-m,
Rg

Em Volt
Es
Volt
(av2)
-m
Rg

Em Volt
Es
Volt

1
100,300,20
1.28
126
85
158
0.89
151
86

2
300,100,20
0.72
187
92
194
1.09
185
106

Table E2  Apparent resistance data for soil type-1 and 2 of table E1, measured with 4-pin method

Probe Separation (ft)
Soil Type-1, Resistance ,
Soil Type-2, Resistance ,

1.0
29.725
89.16

3.0
15.325
45.845

5.0
9.969
29.553

15.0
3.853
9.385

20.0
3.152
6.462

30.0
2.49
3.517

50.0
1.897
1.504

70.0
1.557
0.897

90.0
1.321
0.642

110.0
1.146
0.505

130.0
1.011
0.419

150.0
0.904
0.359

Annex  F

Grounding Methods for High‑Voltage Stations With Grounded Neutrals
(Informative)
(Erdungsmassnahmen fur Hochstspannungsanlagen mit Geerdetem Sternpunkt)

Walter Koch.
 Elektrotechnische Zeitschrift.

Vol. 71, No. 4, pp. 89‑91, Feb. 1950

It is not economically feasible to provide grounding in high‑voltage stations with grounded neutral, which will in to limit contact potentials to ground electrodes and the connected apparatus to less than 125 volts.  One has to deal with a multiplicity of potentials which may be established between the plant and the surroundings under Short-circuit conditions.

Experiments with models show that by making the ground system in the form of a grid, areas within the system can be produced which will be safe.  Means for safe entry into the grounding area will be given.

With a directly grounded neutral point there flows into the system at the fault point the so‑called ground‑fault current instead of the total single‑phase short-circuit ground current (Ungrounded System).  This ground‑fault current depends upon the generating capacity of the power plants in the area and on the impedance of the ground circuit.  The grounding systems of a solidly grounded network will carry a portion of the ground‑fault current which may be a minimum for faults a great distance from the station and may be a maximum, namely the total ground‑fault current, for a fault in the station.

While the grounding systems may be adjusted to eliminate dangerous contact potentials by suppression of ground short‑circuit currents, this is not usually demanded of solidly grounded neutral systems because it does not appear to be practicable.  For ground‑fault currents above 1000 amperes, grounding systems of vast dimensions must be installed in order to meet the usual 125‑volt contact potential requirement.  A numerical example will show this.  The surface area of an outdoor substation may be 250 · 250 meters.  Here one has the possibility of placing a ground plate of 62,500 square meters under the station.  With an average ground resistivity of 100 ohm‑meters and the equivalent circular plate diameter of 280 meters the ground resistance is




or




With such a ground, a ground‑fault current of 5000 amperes will produce a 900-volt potential above the more‑distant surroundings which is many times the potential allowed by VDE.  In spite of this, it has the indisputable advantage that the entire station on this metal plate will have no potentials between parts within itself that are worth mentioning.  For persons inside the station there will not be the slightest danger from undue contact potentials at such a high current.  There would be danger only if at the moment of fault one were to enter or leave the plant or touch it from the outside.  It is not practical to construct such a ground plate.  However, in order not to endanger the personnel of an electrical plant, ways must be sought to fulfill this requirement.

Besides the dangers to personnel, there will be some to the material of the control and communications equipment if it is not provided against.  The sheaths of the control cables provide a connection between the controlled apparatus in the high‑voltage bays and the control point.  Thereby, a fault to ground in the station can cause a very large current to flow through the sheath and melt it.  Communication cables which leave the plant will also conduct ground currents away since intentionally or unintentionally they come into contact with building construction parts.  Thereby, the sheaths acquire the high potential of the station in their vicinity while the conductors approximate the potential of the more-distant surroundings, so that insulation failures may occur.  So likewise the cables of the low‑voltage plant, and the windings of control motors among others may be endangered by large potential differences.  Indeed, for these reasons it is not permissible to rely only on a sufficient interconnection of all apparatus such as circuit breakers, transformer cases, frame parts, etc.  To this all cable sheaths within the plant must also be connected; so likewise the control mechanisms in the switching station to which the control cables are connected.  Basically the entire plant should be provided with a built‑up ground mat for the ground‑fault current, to which all equipment parts in the plant are connected.  So likewise the existing neutral conductors of independent low‑voltage systems should be tied to the ground mat.  By this method there will be the least worry that significant potential differences will arise between the accessible metallic parts of the plant and the plant equipment so protected will be safe from failure.

Now, it is certain that considerable and therefore dangerous potentials can arise between the soil, the floors of buildings on one side and the metallic parts of the plant during the time of faults.  Therefore one must also consider the safety of operating personnel who in the course of their work must touch such metal parts.  For this purpose the operating position may be provided either with an insulated floor capable of withstanding the high potential or with a metallic grid in the floor and tied to the ground mat or provided with both.  Such metallic foot grids have been previously used for protection in Siemens-Schuckert plants with ungrounded star neutral.  They consisted of small meshed wire netting cemented into the floor and tied to the grounding system, and provided absolute protection to persons standing thereon and grasping operating controls in that a highly conducting shunt path was provided between hands and feet.

As mentioned in the introduction, a large metallic plate is a suitable protection against all step potentials and contact potentials within the plant.  Since such a metallic plate installation is not realizable, the question arises on how far one can go in substituting a network of ground straps and the necessary mesh spacing in order to obtain tolerable potential differences.

The investigation of the potential distribution of complicated ground electrode arrangements, which such a ground mat is, is not possible by computation, since one can derive formulae only for simple electrode shapes and even simple combinations of these electrode shapes are not amenable to calculation.  For mesh‑type electrode arrangements with irregular depth of burial which is the way they are used for the purpose of potential control and other complicated grounding structures, one is led to the use of models.  For this purpose such model measurements using an electrolytic tank were undertaken.  A metal container filled with a conducting solution served as the semi‑infinite space for the current diffusion.  Figure F1 shows the circuit of the test arrangement.  The potential distribution for model M can be obtained by a null method using the electrode S, the calibrated potentiometer P and telephone receiver T. In order to reduce the electrolytic effect of the chopped direct current supply on the model, a slowly rotating switch U was placed in the direct current supply leads.

The model of the ground mat consisted of a copper wire 0.2 millimeters in diameter arranged in a square with 120 millimeter sides and set on the surface.  For the usual ground straps with a cross‑section of 30 · 3 millimeters corresponding to an equivalent diameter of 23 millimeters this model represented a replica of a ground system with a length of

Figure F1
Circuit for obtaining potential distribution
Figure F2

Measured potential distribution for various ground mats
Figure F3

Measured potential distribution for various ground mats



or 13.8 meters on a side.  After obtaining the potential distribution, the square was subdivided to contain four squares by the addition of a wire cross, the four subsquares were similarly subdivided until 64 subsquares were attained and in each case the potential inside the square was measured.  As the mesh becomes finer the effect approaches a plate electrode.  In figures F2 - F5 the potential at the center point of each square is given in percent of the potential of the ground mat.  The potential differences which characterize the step potentials and thereby the hazard are according to these figures for fine‑mesh electrodes 11 ‑ 20 percent of the total potential.  The mesh spacing of the mat with 64 meshes is, according to the above‑mentioned model scale, 13.8/8 = 1.7 meters.  The potential distributions in cross‑sections through the mats at A‑B, C‑D, E‑F and G‑H of figures F2 -- F5 are shown in figure F6. In order to determine the effect of only a partial fine mesh inside the outer edge, the arrangement shown in figure F7 was investigated and as shown in figure F8 with further subdivision of a single mesh.  From this it follows that in the area of a fine mesh the same relations (proportions) hold as in the complete meshing of the total grounding area.  The still finer subdivision of a single mesh results in a further raising of the potential inside the mesh, that is, a corresponding decrease of the potential differences and thereby the step potential.

Figure F4
Measured potential distribution for various ground mats
Figure F5
Measured potential distribution for various ground mats
Figure F6
Potential distribution for a ground mat with various mesh densities
ground mat potential = 100 percent
The measurements show, as might be expected, that by using a fine mesh a considerable reduction in potential differences within the mat area can be obtained. Further, it is apparent that small protected areas can be produced by partial matting without completely matting the entire grounding area.  Practical application of such finer meshing can be found principally in outdoor stations in the neighborhood of accessible equipment where the hazard is greatest.

A reduction of the effect, which will not completely eliminate potential differences, can be arrived at by a fill of course grit (gravel) to a depth of about 1 centimeter over such a ground grid.  With this everything practical has been done in order to minimize the hazard, if not to eliminate it entirely.

To be sure, there remain the locations of the passageways to the protected areas which remain a hazard when traveling over them during the time of a fault.  F6 shows the high potential drops at the edges of the wide meshed areas, where step potentials of about 45 percent of the total potential to the ground electrode can be encountered.  If one must obtain absolute safety, then on the passageways one must resort to the so‑called potential ramps in order to obtain a small, and as far as possible, uniform potential drop.  Wooden passageways have likewise already been used in the Siemens-Schuckert works in 200‑kV stations.

Figure F7
Potential distribution for ground mats with fine meshes in portions
Figure F8
Potential distribution for ground mats with fine meshes in portions
The means of potential control through grounding straps buried at progressively deeper depths is shown in principle in figure F9, the effectiveness of which was proved by the leveling off of the potential surface in a model.  figure F10 shows the application of potential control around the footing of a tower when one does not desire to, or is not able to, employ a fence.

The magnitude of the expected step potential for a ground mat depends upon the ground resistance, the short‑circuit current and the mesh density.  If one takes the area of an outdoor substation 250 meters square, then a ground strap around the periphery will be 1000 meters long.  Without regard to the cross connections and matted grounds, the ground resistance of this strap is R = _/_L ln 2L/d; where _ is the ground resistivity (generally 100 ohm‑meters) L is the length of the strap in centimeters and d is the equivalent diameter of the strap as a conductor with a semicircular cross‑section (for the usual ground‑strap d = 2.3 centimeters).  With these figures R=0.36 ohm.  The resistance is thus only twice as great as for a solid plate 250 · 250 meters.  The reactance will be reduced by the cross‑connections which are required for tying in the apparatus to be grounded.

With a short‑circuit current of, for example, 5000 amperes, the voltage to the ground system will be about 1800 volts.  With a ground rating as shown in figure F5 the greatest step potential to be expected will be about 11 ‑ 12 percent of this value, or 200 volts, the effect of which on persons can be reduced effectively by using gravel fill.  According to figure F8, with a mesh spacing of 0.85 meters the potential inside the mesh is 7 percent of the ground mat potential and for a ground mat potential of 1800 volts the step potential can thereby be reduced below 125 volts if necessary.

Figure F9
Potential distribution in a ground mat with ramp
(Curve 1) and without ramp (Curve 2)
The systematic application of the protective measures described makes the separation of the operating ground from the protective ground superfluous.  The separation of operating and protective grounds gives no protection for faults inside the station and from experience these must be considered.  The installation of a separated star neutral ground system requires a tremendous amount of land outside the station.  There is no advantage worth mentioning for this since a protective ground is still required inside the station.  It therefore can only be recom​mended that the star‑neutral point be connected to a suitable ground system as described in the foregoing or otherwise for a separate grounding system to employ the requisite materials for an ample development of the protective ground system.

Figure F10
Potential distribution around a mast footing in the direction A‑B

for a mast with ramp (Curve b) and without ramp (Curve a)
Tying together both systems (protective and operating) has the noteworthy advantage that for a ground fault within the station the ground‑fault current component of the faulted station need not be carried by the ground mat but is conducted directly over the grounding conductors which are tied to the star neutral point.  Also, one has only to reckon with the difference between the total ground‑fault current and the station component, whereby there is a considerable reduction in ground mat potential and step potential.

The overhead ground wire of the outgoing station transmission lines may be advantageously connected to the station ground, and effectively reduce the total ground resistance; this is especially so where the ground wire which appears to be necessary for star neutral grounded systems with high ground‑fault currents is of ample design.

SUMMARY
Large contact and step potentials under fault conditions must be considered in high‑voltage stations using grounded star neutral point.  Potential differences which may endanger cable insulation and low‑voltage apparatus and facilities (for example, windings of control motors) may be eliminated by metallic interconnection of equipment housing, sheaths of control and service cables and their neutral conductors, and the construction parts in the control house.  For protection of personnel at the danger points, narrow meshed ground mats with mesh spacing of about 1 meter will serve.  The potential distribution of such ground mats may be investigated by means of electrolytic tanks.  A separate operating ground for the star neutral point is not recommended, since connection of the latter to a general ground system designed according to the viewpoint outlined herein, has advantages over separation.  Approaches to parts of the ground system which have potential control can be made safe by the so‑called potential ramps.

� Obviously, the same ground gradient problems that exist in a substation yard should not be present within a building.  This will be true provided the floor surface either assures an effective insula�tion from earth potentials, or else is effectively equivalent to a conductive plate or close mesh grid that is always at substation ground potential, including the building structure and fixtures.


	Therefore, even in a wholly indoor substation it may be essential to consider some of the possible hazards from perimeter gradients (at building entrances) and from transferred potentials described in clause 8.  Furthermore, in the case of indoor gas�insulated facilities, the effect of circulating enclosure currents may be of concern, as discussed in clause 10.


� The greater impedance offered to steep front surges will  somewhat increase the voltage drop in ground leads to the grid system, and decrease the effectiveness of the more distant parts of the grid.  Offsetting this in large degree is the fact that the human body apparently can tolerate far greater current magnitudes in the case of lightning surges than in the case of 50 or 60 Hz currents.


� Information on references can be found in clause 2.


� ANSI publications are available from the Sales Department, American National Standards Institute, 1430 Broadway, New York, NY 10018.


� IEEE publications are available from the Institute of Electrical and Electronics  Engineers, 445 Hoes Lane, P.O. Box 1331, Piscataway, NJ 08854-1331.


�  The numbers in brackets correspond to those bibliographical items in Annex A.


� Typically, these conditions can be met in places that are not accessible to the public, such as in switchyards protected by fences or walls, etc. Depending on specific circumstances, an assessment should be made if a 50 kg criterion equation (8) ought to be used for areas outside the fence.


�Expressions for the ground resistance of the foot given in IEEE Standard 80-1986 equations (16) to (19) were based on the simple procedure for hemispheric electrodes.  This simplification gave lower value of the ground resistance of the foot.  The error was significant for low values of the depth of the surface layer.  The new revised expressions for the ground resistance of the foot given in this standard are based on the circular plate representation of the foot.





� One possible exception is grounding of the secondaries of potential and current transformers.  The grounding of such devices usually must be restricted to a single point to avoid any parallel path that could cause undesirable circulation of currents affecting the performance of relays and metering devices.


� However, despite all measures described, the presence of circulating currents can cause different parts of the GIS metal housing to have a slightly different potential to ground.  Though the resulting voltage differences are small and generally of no concern with regard to a shock hazard, accidental metallic bridging of adjacent enclosures can cause annoying sparks.


�  The direct effect of TEV on humans may not be fatal, but its secondary effect on personnel should be of concern to the design engineer and the manufacturer.  In addition, TEV might necessitate that more stringent electromagnetic compatibility requirements be considered for auxiliary equipment. 


� It might be argued that the concrete slab, being a fairly good conductor itself, could produce a more uniform voltage at the floor level if no current would flow into the reinforcing bars from the ground system.  If the bars are connected, the electrical field in the earth between the bars of the slab and the underlying grid would be zero. (As both mats are at the same potential, hardly any current would flow out of the bars into the concrete and toward the ground grid.) Therefore, the concrete with reinforcing bars will produce a substantially uniform potential field across the floor surface.


� As discussed in 12.5, it is a common practice to have a thin layer of surface material overlaying the grounded area of a substation.  It could appear that such a high resistivity layer, having the layer height h, much less than the depth of the grounding system, might worsen both the step and touch voltage.  However, this is not the case.  The surface material is used to increase the contact resistance between a person’s foot and the earth surface.  Thus, for a given maximum allowable body current, considerably higher step and touch voltages can be allowed if a surface material is present.


� Ollendorf neglects the cooling effect of evaporated moisture in calculating I�SÍMBOLO 165 \f "Symbol" \s 8�� [B108].


� In most calculations it is usually permissible to assume a ratio of X2/X1 equal to unity, and hence X1=X2, especially if an appreciable percentage of the positive sequence reactance to the point of fault is that of static apparatus and transmission lines.


� Unless otherwise specified, the remainder of the guide will use the term mesh voltage (Em) to mean the touch voltage at the center of the corner mesh.  However, the mesh voltage may not be the worst case touch voltage if ground rods are located near the perimeter, or if the mesh spacing near the perimeter is small.  In these cases, the touch voltage at the corner of the grid may exceed the corner mesh voltage.


� References [B119] and [B120] contain the early (preballot) versions of Sections 1-6 and 7 - 12 of this guide.  As such, neither the equations nor the text of these references should be used in lieu of the corresponding material of the guide.





    � That is, not accessible to the general public.


� English translation by T. W. Stringfield.  Some portions on Petersen coil systems and German (VDE) regulations omitted.


� References [B119] and [B120] contain the early (preballot) versions of Sections 1-6 and 7 - 12 of this guide.  As such, neither the equations nor the text of these references should be used in lieu of the corresponding material of the guide.





    � That is, not accessible to the general public.


� English translation by T. W. Stringfield.  Some portions on Petersen coil systems and German (VDE) regulations omitted.





PÁGINA  
142

_910003368.unknown

_910003727.unknown

_910003818.unknown

_910003839.unknown

_910003848.unknown

_910003852.unknown

_910003854.unknown

_910003855.unknown

_910003853.unknown

_910003850.unknown

_910003851.unknown

_910003849.unknown

_910003844.unknown

_910003846.unknown

_910003847.unknown

_910003845.unknown

_910003842.unknown

_910003843.unknown

_910003841.unknown

_910003828.unknown

_910003834.unknown

_910003837.unknown

_910003838.unknown

_910003836.unknown

_910003831.unknown

_910003833

_910003830

_910003822.unknown

_910003825.unknown

_910003827

_910003824.unknown

_910003820.unknown

_910003821.unknown

_910003819.unknown

_910003785.unknown

_910003801.unknown

_910003810.unknown

_910003814.unknown

_910003816.unknown

_910003817.unknown

_910003815.unknown

_910003812

_910003813.unknown

_910003811.unknown

_910003805.unknown

_910003808.unknown

_910003809

_910003806

_910003803

_910003804.unknown

_910003802.unknown

_910003793.unknown

_910003797.unknown

_910003799.unknown

_910003800.unknown

_910003798.unknown

_910003795.unknown

_910003796.unknown

_910003794.unknown

_910003789

_910003791.unknown

_910003792.unknown

_910003790.unknown

_910003787.unknown

_910003788.unknown

_910003786.unknown

_910003744.unknown

_910003752.unknown

_910003776

_910003781

_910003783

_910003784.unknown

_910003782

_910003779

_910003780

_910003777.unknown

_910003759.unknown

_910003772.unknown

_910003774

_910003775

_910003773

_910003762.unknown

_910003770.unknown

_910003771.unknown

_910003763.unknown

_910003769.unknown

_910003760.unknown

_910003755.unknown

_910003757.unknown

_910003754.unknown

_910003748.unknown

_910003750.unknown

_910003751.unknown

_910003749.unknown

_910003746.unknown

_910003747.unknown

_910003745.unknown

_910003735.unknown

_910003740.unknown

_910003742.unknown

_910003743.unknown

_910003741.unknown

_910003738.unknown

_910003739

_910003737

_910003731.unknown

_910003733.unknown

_910003734

_910003732.unknown

_910003729.unknown

_910003730.unknown

_910003728.unknown

_910003694.unknown

_910003711.unknown

_910003719.unknown

_910003723.unknown

_910003725.unknown

_910003726.unknown

_910003724.unknown

_910003721

_910003722.unknown

_910003720.unknown

_910003715.unknown

_910003717.unknown

_910003718

_910003716

_910003713

_910003714.unknown

_910003712.unknown

_910003703.unknown

_910003707.unknown

_910003709.unknown

_910003710.unknown

_910003708.unknown

_910003705.unknown

_910003706.unknown

_910003704.unknown

_910003698

_910003701.unknown

_910003702.unknown

_910003699.unknown

_910003696.unknown

_910003697.unknown

_910003695.unknown

_910003390.unknown

_910003398.unknown

_910003686

_910003690

_910003692

_910003693.unknown

_910003691

_910003688

_910003689

_910003687.unknown

_910003402.unknown

_910003682.unknown

_910003684

_910003685

_910003683

_910003404.unknown

_910003680.unknown

_910003681.unknown

_910003406.unknown

_910003679.unknown

_910003403.unknown

_910003400.unknown

_910003401.unknown

_910003399.unknown

_910003394.unknown

_910003396.unknown

_910003397.unknown

_910003395.unknown

_910003392.unknown

_910003393.unknown

_910003391.unknown

_910003382.unknown

_910003386.unknown

_910003388.unknown

_910003389.unknown

_910003387.unknown

_910003384.unknown

_910003385.unknown

_910003383.unknown

_910003375.unknown

_910003378.unknown

_910003380.unknown

_910003377.unknown

_910003372.unknown

_910003373.unknown

_910003370.unknown

_910003335

_910003351.unknown

_910003360.unknown

_910003364.unknown

_910003366.unknown

_910003367.unknown

_910003365.unknown

_910003362.unknown

_910003363.unknown

_910003361.unknown

_910003355.unknown

_910003357.unknown

_910003358.unknown

_910003356.unknown

_910003353.unknown

_910003354.unknown

_910003352.unknown

_910003343.unknown

_910003347.unknown

_910003349.unknown

_910003350.unknown

_910003348.unknown

_910003345.unknown

_910003346.unknown

_910003344.unknown

_910003339.unknown

_910003341.unknown

_910003342.unknown

_910003340.unknown

_910003337.unknown

_910003338.unknown

_910003336

_906231332.unknown

_910003318.unknown

_910003326.unknown

_910003330

_910003333

_910003334

_910003332

_910003328

_910003329

_910003327.unknown

_910003322.unknown

_910003324

_910003325

_910003323

_910003320.unknown

_910003321.unknown

_910003319.unknown

_906743467.unknown

_906743857.unknown

_906745112.unknown

_910003316.unknown

_910003317.unknown

_910003315.unknown

_910003314.unknown

_906743924.unknown

_906743679.unknown

_906743767.unknown

_906743543.unknown

_906743587.unknown

_906232007.unknown

_906232530.unknown

_906743109.unknown

_906232305.unknown

_906231642.unknown

_906231934.unknown

_906231542.unknown

_906227699.unknown

_906230588.unknown

_906231064.unknown

_906231245.unknown

_906231006.unknown

_906230336.unknown

_906230488.unknown

_906228443.unknown

_901830826.unknown

_901833051.unknown

_906227156.unknown

_903418921.unknown

_901832656.unknown

_901832658.unknown

_901832126.unknown

_877157473

_877168524.unknown

_877183033

_901830474.unknown

_877171283.unknown

_877167962.unknown

_877156541.unknown

